## S-NEM2300-bus.ecf
Component | Base Power | Base Voltage | Frequency | Field current | Number of poles | Rs | Xl | X0 | Xd | Xq | Xpd | Xpq | Xppd | Xppq | Tpd0 | Tpq0 | Tppd0 | Tppq0 | Xc | Stator connection | Number of mass | H [5] | Kd [5] | D [5] | Kij [4] | Dij [4] | F [4] | H (Exciter) | Kd (Exciter) | D (Exciter) | K (Generator-exciter) | D (Generator-exciter) | Exciter Type | Exciter control | Mechanical control | Saturation | d-axis saturation curve points | q-axis saturation curve points | Imd [10] | Fluxmd [10] | Imq [10] | Fluxmq [10] | d-axis damper | q-axis damper | Type of bus | Voltage | Angle | Active power | Reactive power | Reactive power minimum | Reactive power maximum | MVAr | kV | MVA
Machine | sBase | vBase | Frequency | FieldCurrent | PoleNumber | Rs | Xls | X0 | Xd | Xq | Xpd | Xpq | Xppd | Xppq | Tpd0 | Tpq0 | Tppd0 | Tppq0 | Xc | Connection | MassNumber | InertiaConstant | AbsoluteDamping | SelfDamping | Stiffness | MutualDamping | Fraction | H_EXC | K_EXC | D_EXC | K_GEN_EXC | D_GEN_EXC | ExciterType | ExciterControl | MechanicalControl | Saturation_Type | NdSat | NqSat | Im_Points | Fluxm_Points | Imq_Points | Fluxmq_Points | dAxisDamper | qAxisDamper | lfType | lfVolt | lfAngle | lfP | lfQ | lfQmin | lfQmax | MVAr | kV | MVA
| (VA) | (V) | (Hz) | (A) |  | (pu) | (pu) | (pu) | (pu) | (pu) | (pu) | (pu) | (pu) | (pu) | (s) | (s) | (s) | (s) | (pu) |  |  | (s) | (Nm/rad/s) | (Nm/rad/s) | (Nm/rad) | (Nm/rad/s) |  | (s) | (Nm/rad/s) | (Nm/rad/s) | (Nm/rad) | (Nm/rad/s) | [6 empty] | (pu) | (pu) | (pu) | (pu) |  |  |  | (pu) | (°) | (W) | (var) | (var) | (var) | MVAr | kV | MVA
gen_1002_1 | 848605419.222452 | 23000 | 50 | 1300 | 4 | 0 | 0.190636673497502 | 0.56751502476334 | 2.27006009905336 | 2.15885508540102 | 0.320205435705767 | 0.253126455120051 | 0.254731010818402 | 0.254731010818402 | 8.64181632340699 | 0.375239718798548 | 0.046943271899363 | 0.136205370032741 | 0 | 1 | 1 | 3.16825912071811 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.113990566016044 0.375405293004038 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | E | 1.01556 | 0 | 431893342.324 | -24521463.398 | -232885600.966588 | 361080897.667566 | 361.0809 | 23 | 848.6054
gen_1003_2 | 911269176.985324 | 23000 | 50 | 1300 | 4 | 0 | 0.190670949609717 | 0.5536047385564725 | 2.21441895422589 | 2.14820705504363 | 0.331301903893286 | 0.258212115779878 | 0.245573479835396 | 0.245573479835396 | 8.42964508440159 | 0.389128416377935 | 0.0462607079501264 | 0.135833965283772 | 0 | 1 | 1 | 3.15421162367985 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.112666115340763 0.368391471655103 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02626 | 1.9755 | 624407378.34601 | 64816888.35895839 | -186429364.080189 | 447694821.266016 | 447.6948 | 23 | 911.2692
gen_1004_3 | 914521020.424575 | 23000 | 50 | 1300 | 4 | 0 | 0.190881724390006 | 0.5580462366286325 | 2.23218494651453 | 2.15366160325371 | 0.332113386869733 | 0.254357078468506 | 0.251368805532902 | 0.251368805532902 | 8.397773353286089 | 0.383822161483113 | 0.0476119478437584 | 0.135908252601512 | 0 | 1 | 1 | 3.13463414354902 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.117853057886264 0.371673717224426 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.999 | 5.4272 | 650401460.230983 | 17188369.3068953 | -259347073.892131 | 388821155.851102 | 388.8212 | 23 | 914.521
gen_1005_4 | 915047054.038756 | 23000 | 50 | 1300 | 4 | 0 | 0.185403954635132 | 0.5656604292314275 | 2.26264171692571 | 2.16079874452307 | 0.32247932254998 | 0.250932273443153 | 0.246066220155838 | 0.246066220155838 | 8.394984227583739 | 0.386250622768421 | 0.0469641184676904 | 0.135715317474026 | 0 | 1 | 1 | 3.13492437275127 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.115268518456961 0.360750868524648 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00251 | 5.6574 | 631753907.6734401 | 37213374.1970971 | -183809605.420828 | 443446216.774394 | 443.4462 | 23 | 915.0471
gen_1012_1 | 41101297.5615542 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.157411517668515 | 0.29039684866072 | 1.16158739464288 | 0.5928788602156559 | 0.280712300090119 | 0.188905356998672 | 0.188905356998672 | 10 | 9.297813491011039 | 0.152946320953779 | 0.0539238605838269 | 0.01 | 0 | 1 | 1 | 4.03096771309245 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.13177192842029 0.592974049122538 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01546 | 9.736599999999999 | 30226535.7711347 | 2132831.26498573 | -2825488.00646961 | 2775275.80510248 | 2.7753 | 0.69 | 41.1013
gen_1013_1 | 45462846.3133704 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.15289566900814 | 0.28746587569476 | 1.14986350277904 | 0.607215649646707 | 0.280331428875215 | 0.189256160524907 | 0.189256160524907 | 10 | 9.44040461014956 | 0.15697254223167 | 0.0526899192777462 | 0.01 | 0 | 1 | 1 | 4.10389041107241 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.135691078041913 0.587066242041998 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01729 | 9.7303 | 32122197.2278725 | 3847882.42996335 | -5176808.58559278 | 5342418.080064651 | 5.3424 | 0.69 | 45.4628
gen_1014_1 | 28477100.0574343 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.152158027030528 | 0.283157725875615 | 1.13263090350246 | 0.581197085483465 | 0.287706468353048 | 0.185665983258747 | 0.185665983258747 | 10 | 9.42527587695513 | 0.156126313571585 | 0.0534463943126611 | 0.01 | 0 | 1 | 1 | 4.07182763364306 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.131101594094653 0.599824795256835 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.0126 | 8.6286 | 19277781.1919969 | 463685.144224996 | -510663.52698796 | 515716.733953799 | 0.51572 | 0.69 | 28.4771
gen_1017_1 | 853151746.194251 | 23000 | 50 | 1300 | 4 | 0 | 0.189457268492132 | 0.5467449585580625 | 2.18697983423225 | 1.60592827188673 | 0.325645458190138 | 1.08153077109002 | 0.203768784317002 | 0.203768784317002 | 8.390679817018761 | 2.05102453759257 | 0.0632392940051854 | 0.178434604043653 | 0 | 1 | 1 | 3.29391465716064 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09833795538311819 0.366664496996999 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01122 | 13.2453 | 565935071.0644649 | 76768217.4324051 | -271241277.304944 | 439832941.857143 | 439.8329 | 23 | 853.1517
gen_1018_2 | 828587737.327442 | 23000 | 50 | 1300 | 4 | 0 | 0.193715469417721 | 0.543606385216815 | 2.17442554086726 | 1.64286390568612 | 0.327735764552229 | 1.11781046042717 | 0.19805634210119 | 0.19805634210119 | 8.246653611663101 | 1.97290236046906 | 0.0611450468741357 | 0.181748822734552 | 0 | 1 | 1 | 3.21804560035467 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09430904589057899 0.378953377043386 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01837 | 13.6342 | 664180290.584602 | 116850947.170548 | -272264737.280784 | 421638958.235597 | 421.639 | 23 | 828.5877
gen_1019_3 | 824955784.7308 | 23000 | 50 | 1300 | 4 | 0 | 0.193056594339386 | 0.55025156856171 | 2.20100627424684 | 1.66660411743992 | 0.328312649695319 | 1.08521066677386 | 0.203563261227636 | 0.203563261227636 | 8.521538339395191 | 1.99273348299945 | 0.0631405915910751 | 0.182128424060997 | 0 | 1 | 1 | 3.35375534132123 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09762546354182999 0.380439872584655 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02332 | 14.499 | 630779430.353494 | 123099154.396053 | -264036246.150499 | 427189790.036436 | 427.1898 | 23 | 824.9558
gen_1020_4 | 815543500.3673661 | 23000 | 50 | 1300 | 4 | 0 | 0.195112073822413 | 0.54208183993693 | 2.16832735974772 | 1.64989939148594 | 0.322611822450992 | 1.10005332359257 | 0.207593269594805 | 0.207593269594805 | 8.33145218183744 | 2.00808816904044 | 0.0618033530248702 | 0.180988344361074 | 0 | 1 | 1 | 3.27817697316408 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0959758984792512 0.37806775526139 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01577 | 14.6195 | 660810311.423638 | 92798215.07611869 | -270017779.694172 | 424976144.654024 | 424.9761 | 23 | 815.5435
gen_1022_1 | 100102913.2 | 16000 | 50 | 1300 | 4 | 0 | 0.148720965130371 | 0.2772817670186625 | 1.10912706807465 | 0.6056825404295 | 0.24084191412814 | 0.188113821326336 | 0.188113821326336 | 10 | 6.08867993660417 | 0.239980493170395 | 0.0768487544256006 | 0.01 | 0 | 1 | 1 | 4.06486977210152 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.02669 | 4.9519 | 81956833.3770882 | 3742154.55035185 | -24477591.6519596 | 43677229.1879432 | 43.6772 | 16 | 100.1029
gen_1030_4 | 99532006.9049927 | 16000 | 50 | 1300 | 4 | 0 | 0.152785054653371 | 0.253264289914165 | 1.01305715965666 | 0.702534276496153 | 0.22686294478314 | 0.205493323253468 | 0.205493323253468 | 10 | 9.01301313512127 | 0.230851957343053 | 0.0730565607765689 | 0.01 | 0 | 1 | 1 | 4.4912705247649 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01913 | 4.6106 | 77326783.8781388 | -3508512.74594665 | -28311724.5702714 | 41149808.1746824 | 41.1498 | 16 | 99.532
gen_1031_1 | 90588925.5829901 | 11000 | 50 | 1300 | 4 | 0 | 0.200671900155139 | 0.35651549306442 | 1.42606197225768 | 0.725259874475119 | 0.360715030336287 | 0.215285751172295 | 0.215285751172295 | 10 | 6.74459750028513 | 0.103638262345921 | 0.06645807624247391 | 0.01 | 0 | 1 | 1 | 3.96822433128487 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0650091051340103 0.238240595932258 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.95282 | 24.2299 | 55970990.0665401 | -7301094.34132907 | -28927321.1265099 | 28842300.4899453 | 28.8423 | 11 | 90.5889
gen_1034_1 | 643693602.205161 | 22000 | 50 | 1300 | 4 | 0 | 0.182184809171688 | 0.5740259373863225 | 2.29610374954529 | 2.2181340783881 | 0.337903481459578 | 0.212362598386127 | 0.212362598386127 | 10 | 3.65829917187236 | 0.376136706941249 | 0.0437073619368835 | 0.01 | 0 | 1 | 1 | 2.78987184259761 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97349 | 14.0395 | 405051269.335069 | 36037735.3830287 | -101981858.3922 | 202223581.927363 | 202.2236 | 22 | 643.6936
gen_1036_3 | 645286667.25168 | 22000 | 50 | 1300 | 4 | 0 | 0.181209346052259 | 0.551748258512235 | 2.20699303404894 | 2.21355740551371 | 0.332660602351355 | 0.208229321039747 | 0.208229321039747 | 10 | 3.82475675741222 | 0.389375473775342 | 0.0437813889640686 | 0.01 | 0 | 1 | 1 | 2.87278849575017 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.93205 | 14.8303 | 407774992.019047 | -93842624.7742008 | -114726124.28 | 210926806.9 | 210.9268 | 22 | 645.2867
gen_1037_4 | 628984984.9482071 | 22000 | 50 | 1300 | 4 | 0 | 0.178712068224186 | 0.5709313606948125 | 2.28372544277925 | 2.283065260523 | 0.332178768790921 | 0.207403352959082 | 0.207403352959082 | 10 | 3.76583915847132 | 0.378321451282338 | 0.0438144045604672 | 0.01 | 0 | 1 | 1 | 2.81364450740721 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97558 | 14.4213 | 426516177.432253 | 42106627.5972186 | -98668065.3292453 | 200851186.675485 | 200.8512 | 22 | 628.985
gen_1038_1 | 343073364.149896 | 15400.0 | 50 | 1300 | 4 | 0 | 0.236584797610366 | 0.41674134733216 | 1.66696538932864 | 0.776077050098032 | 0.420243821831234 | 0.306640662051807 | 0.306640662051807 | 10 | 14.6442208761923 | 0.0472368835955858 | 0.0295899051190121 | 0.01 | 0 | 1 | 1 | 3.25332150796009 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.253967852977803 0.856423022171878 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97897 | 26.9607 | 246363716.542234 | 1110589.56654603 | -87762758.7602939 | 88059949.08506981 | 88.0599 | 15.4 | 343.0734
gen_1039_2 | 338426626.157714 | 15400.0 | 50 | 1300 | 4 | 0 | 0.239894437453221 | 0.42754219776648 | 1.71016879106592 | 0.7724022796133529 | 0.409458185624925 | 0.30078968214998 | 0.30078968214998 | 10 | 14.8640386024794 | 0.0464558569884393 | 0.0302604074398451 | 0.01 | 0 | 1 | 1 | 3.21982772525749 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.253132513660239 0.873024938468519 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97805 | 26.9149 | 246535469.41532 | -1167842.6247424 | -88673278.2728039 | 89141724.98094849 | 89.1417 | 15.4 | 338.4266
gen_1040_3 | 341423653.126345 | 15400.0 | 50 | 1300 | 4 | 0 | 0.240901087828889 | 0.417865915450965 | 1.67146366180386 | 0.762259163425909 | 0.401581730715756 | 0.296873828812817 | 0.296873828812817 | 10 | 14.9148540720392 | 0.0457911968962289 | 0.0302604992726794 | 0.01 | 0 | 1 | 1 | 3.29186792900087 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.253118924319278 0.834528490301268 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98407 | 26.8824 | 248465284.474285 | 13476640.8302221 | -87966344.8969368 | 89382511.2764724 | 89.3825 | 15.4 | 341.4237
gen_1041_4 | 336309318.444924 | 15400.0 | 50 | 1300 | 4 | 0 | 0.239047732157609 | 0.4330380999159775 | 1.73215239966391 | 0.781009434596542 | 0.409013047951134 | 0.3057972905459 | 0.3057972905459 | 10 | 14.8518670666396 | 0.0459985336584505 | 0.0300360310875648 | 0.01 | 0 | 1 | 1 | 3.48995867577754 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.258577903325204 0.841955336298374 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98186 | 26.8985 | 256483332.773739 | 9456149.26232807 | -89550170.6256066 | 86856619.62949671 | 86.8566 | 15.4 | 336.3093
gen_1042_5 | 333510404.178291 | 15400.0 | 50 | 1300 | 4 | 0 | 0.238222133323294 | 0.4205071275938075 | 1.68202851037523 | 0.754270109408349 | 0.410040563086595 | 0.305749526773102 | 0.305749526773102 | 10 | 14.8491940268893 | 0.0466696398595814 | 0.029305506996375 | 0.01 | 0 | 1 | 1 | 3.48183408126282 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.260111580579542 0.8521947222002551 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98377 | 26.8865 | 245363071.142822 | 13794420.3463584 | -87022274.6504471 | 88508224.52739809 | 88.5082 | 15.4 | 333.5104
gen_1043_6 | 340135576.679022 | 15400.0 | 50 | 1300 | 4 | 0 | 0.231587816122267 | 0.419831816410855 | 1.67932726564342 | 0.763275312474882 | 0.410694913491968 | 0.305164144053601 | 0.305164144053601 | 10 | 14.7503153768795 | 0.0453982998013962 | 0.030080075807143 | 0.01 | 0 | 1 | 1 | 3.53615241267253 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.25100596891134 0.8437789681557329 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98556 | 26.9119 | 242463117.731816 | 17971023.5964432 | -87179575.0621241 | 89779203.9635126 | 89.7792 | 15.4 | 340.1356
gen_1044_1 | 832440999.925509 | 23000 | 50 | 1300 | 4 | 0 | 0.19137518667113 | 0.556526879117795 | 2.22610751647118 | 1.60399694923274 | 0.318752726123305 | 1.1182657509669 | 0.20690619433634 | 0.20690619433634 | 8.28933818250556 | 2.04649544797712 | 0.0611245826061815 | 0.184126026728563 | 0 | 1 | 1 | 3.23862476497889 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.095430822324194 0.371389472297346 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9989400000000001 | 6.2795 | 641205869.3838681 | -79220898.5881729 | -178210467.950369 | 411241218.333378 | 411.2412 | 23 | 832.441
gen_1058_1 | 546171568.101272 | 21000 | 50 | 1300 | 4 | 0 | 0.239809837361611 | 0.5614527409493451 | 2.24581096379738 | 2.14879135707719 | 0.35950926054162 | 0.72475032453197 | 0.277527202355512 | 0.277527202355512 | 5.92467431301158 | 0.469903636420704 | 0.0217504555018153 | 0.041068053457886 | 0 | 1 | 1 | 7.82370411843527 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0566004980416293 0.217275354504841 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9880100000000001 | 4.3351 | 409952588.354057 | 8714090.536399739 | -122928439.04081 | 275952247.070405 | 275.9522 | 21 | 546.1716
gen_1059_1 | 46106279.0306169 | 11500.0 | 50 | 1300 | 4 | 0 | 0.189680992418667 | 0.4018746331973825 | 1.60749853278953 | 0.916542787935585 | 0.394296536200214 | 0.237086805154802 | 0.237086805154802 | 10 | 6.01085570453201 | 0.0514339772914536 | 0.0705133091608994 | 0.01 | 0 | 1 | 1 | 3.35744332893006 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.134435962981544 0.360411761194351 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01502 | 25.6233 | 0 | 3290227.54875435 | -12997324.2728971 | 16032279.4052772 | 16.0323 | 11.5 | 46.1063
gen_1060_2 | 46533268.4993628 | 11500.0 | 50 | 1300 | 4 | 0 | 0.191603294584784 | 0.40011123475508 | 1.60044493902032 | 0.88004660837166 | 0.389005247015879 | 0.245533298791852 | 0.245533298791852 | 10 | 5.95436197144212 | 0.0504694285034202 | 0.0705786031519994 | 0.01 | 0 | 1 | 1 | 3.22030340120615 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.136476117643761 0.365882395888213 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.94492 | 31.4882 | 30398959.6087625 | -9755064.226825161 | -13161567.7549504 | 15819799.4363727 | 15.8198 | 11.5 | 46.5333
gen_1067_1 | 30512377.3106886 | 11000 | 50 | 1300 | 4 | 0 | 0.207373877484351 | 0.2858603513795525 | 1.14344140551821 | 0.735210589566743 | 0.374614851844439 | 0.266868610015779 | 0.266868610015779 | 10 | 0.278572612223215 | 0.0103215665838216 | 0.0101880275546573 | 0.01 | 0 | 1 | 1 | 6.92948226211593 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.91609 | 21.5529 | 22593470.7990981 | 11096846.1899283 | -26083109.61 | 17861497.78 | 17.8615 | 11 | 30.5124
gen_1068_2 | 29600267.0221357 | 11000 | 50 | 1300 | 4 | 0 | 0.208864602590911 | 0.2826016265336425 | 1.13040650613457 | 0.728088686738377 | 0.3727067901665 | 0.259144375379954 | 0.259144375379954 | 10 | 0.282933143766713 | 0.0104268435533158 | 0.0100554152012337 | 0.01 | 0 | 1 | 1 | 6.88583802017383 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.04149 | 21.4047 | 20559208.2879526 | -161384.91215324 | -10895512.1632079 | 13182744.6830459 | 13.1827 | 11 | 29.6003
gen_1069_1 | 210894545.504451 | 15750.00 | 50 | 1300 | 4 | 0 | 0.143658924385905 | 0.6296311295412025 | 2.51852451816481 | 2.44465301940264 | 0.273239205386303 | 0.668168241571332 | 0.200497999039292 | 0.200497999039292 | 13.2996721277945 | 1.95170033254032 | 0.046465432904195 | 0.203306559700426 | 0 | 1 | 1 | 5.60216317037749 | 0.0108735563005088 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.189182514905347 0.776961018662457 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.06298 | 35.2488 | 151998828.257293 | -1971999.90038797 | -46317055.2711485 | 92517856.91134459 | 92.5179 | 15.75 | 210.8945
gen_1070_1 | 207096134.014428 | 15750.00 | 50 | 1300 | 4 | 0 | 0.144044353253208 | 0.6325718445101525 | 2.53028737804061 | 2.40724545206293 | 0.268120021589217 | 0.666805989973876 | 0.193713038411737 | 0.193713038411737 | 13.196043761936 | 1.90006118166191 | 0.0482392417188268 | 0.203061292059138 | 0 | 1 | 1 | 5.74241753861564 | 0.0106779984449619 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.193462500094855 0.779293112680293 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.0576 | 35.3963 | 147744403.827981 | -8130281.769632269 | -45327133.3475836 | 92381018.4569456 | 92.381 | 15.75 | 207.0961
gen_1071_1 | 209434487.03438 | 15750.00 | 50 | 1300 | 4 | 0 | 0.142698498049751 | 0.6456171243219875 | 2.58246849728795 | 2.35031908062124 | 0.272531327420427 | 0.683273629018245 | 0.195017864987254 | 0.195017864987254 | 13.2585954592563 | 1.9208578249251 | 0.0467677966958843 | 0.201089784744219 | 0 | 1 | 1 | 5.53843118465086 | 0.0107622134504956 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.19297199129581 0.746550194930565 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.06354 | 35.2742 | 157048257.883772 | -1246573.9881143 | -46343845.6792599 | 92833654.65915379 | 92.8337 | 15.75 | 209.4345
gen_1072_1 | 210867295.503616 | 15750.00 | 50 | 1300 | 4 | 0 | 0.145156730487943 | 0.6346908378613875 | 2.53876335144555 | 2.33866764679505 | 0.274693726127897 | 0.660283152659773 | 0.192910465116799 | 0.192910465116799 | 13.1520820163889 | 1.92749650900904 | 0.046170137693407 | 0.201162778859516 | 0 | 1 | 1 | 5.50961575333495 | 0.0110216279967455 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.189188495927397 0.75222760741245 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.06263 | 35.3296 | 150918810.79843 | -2217124.68539341 | -45439055.4612447 | 92899343.4242263 | 92.8993 | 15.75 | 210.8673
gen_1074_2 | 108814849.924343 | 12500.0 | 50 | 1300 | 4 | 0 | 0.123382624990353 | 0.2449191144704818 | 0.979676457881927 | 0.680828503818484 | 0.2621925007869 | 0.170055595806334 | 0.170055595806334 | 10 | 7.30358025245764 | 0.172023725859122 | 0.0734919211221929 | 0.01 | 0 | 1 | 1 | 3.27968615151476 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.96354 | 21.9299 | 45545313.9887114 | -11729304.5770481 | -28482909.7341048 | 28699369.6373887 | 28.6994 | 12.5 | 108.8148
gen_1075_3 | 110332978.322869 | 12500.0 | 50 | 1300 | 4 | 0 | 0.122580307903374 | 0.25195615897514 | 1.00782463590056 | 0.700514080597553 | 0.267101460130338 | 0.170680748220067 | 0.170680748220067 | 10 | 7.26745661867469 | 0.171489330569981 | 0.0723584957847325 | 0.01 | 0 | 1 | 1 | 3.37318986444594 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9702499999999999 | 22.2663 | 49672188.1388005 | -3454938.03172465 | -29698734.8206574 | 28623892.5730577 | 28.6239 | 12.5 | 110.333
gen_1078_6 | 96487685.0574277 | 12500.0 | 50 | 1300 | 4 | 0 | 0.127947661516862 | 0.2316025956789962 | 0.926410382715985 | 0.54084188815055 | 0.250427186370427 | 0.182677759224316 | 0.182677759224316 | 10 | 8.214832701827991 | 0.153802419046406 | 0.0535696149190469 | 0.01 | 0 | 1 | 1 | 3.1388534370102 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00307 | 22.4341 | 43233176.6436034 | -13684934.6880528 | -29799463.4255767 | 31887023.3734837 | 31.887 | 12.5 | 96.4877
gen_1079_7 | 98025247.76211941 | 12500.0 | 50 | 1300 | 4 | 0 | 0.130957778056758 | 0.2308515359892045 | 0.923406143956818 | 0.539044667238742 | 0.25124353668428 | 0.181141554300557 | 0.181141554300557 | 10 | 8.19016397855906 | 0.155817796894116 | 0.0514716198998038 | 0.01 | 0 | 1 | 1 | 3.17279280964658 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01275 | 22.5133 | 41671530.7017323 | -6342826.474661751 | -30362434.6183613 | 30880851.8911945 | 30.8809 | 12.5 | 98.0252
gen_1080_8 | 96507463.8390634 | 12500.0 | 50 | 1300 | 4 | 0 | 0.130625074540055 | 0.2361729249061318 | 0.944691699624527 | 0.563116229017335 | 0.252504222534201 | 0.175239341291599 | 0.175239341291599 | 10 | 7.97789497352744 | 0.152776010310045 | 0.0526343136359775 | 0.01 | 0 | 1 | 1 | 3.15364401173219 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.02419 | 22.4156 | 43078475.87842049 | 2735294.89369369 | -30148387.4194324 | 31233938.283124 | 31.2339 | 12.5 | 96.5075
gen_1081_5 | 835119563.40652 | 23000 | 50 | 1300 | 4 | 0 | 0.193636014764477 | 0.5533626668161875 | 2.21345066726475 | 1.65354417519325 | 0.31367533963473 | 1.0908238255729 | 0.20690878117187 | 0.20690878117187 | 8.50451356032886 | 1.99137753980123 | 0.0614381766491383 | 0.1797789244466 | 0 | 1 | 1 | 3.32030633851886 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0961563939831685 0.368083550478704 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01885 | 1.7728 | 601922860.507365 | 68420609.5867701 | -155004466.757959 | 409513369.222329 | 409.5134 | 23 | 835.1196
gen_1082_6 | 829493444.249593 | 23000 | 50 | 1300 | 4 | 0 | 0.195409033201635 | 0.553613759516535 | 2.21445503806614 | 1.61763212694176 | 0.323817126925599 | 1.10297605503616 | 0.205219897416048 | 0.205219897416048 | 8.34280464674567 | 2.04065722653568 | 0.0614552841114998 | 0.184893002607394 | 0 | 1 | 1 | 3.21484749294817 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09809677956542 0.365695381680317 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00955 | 1.7506 | 594185006.5023229 | 28983092.4149698 | -151154267.766568 | 409293647.633433 | 409.2936 | 23 | 829.4934
gen_1084_1 | 52317514.8501992 | 11000 | 50 | 1300 | 4 | 0 | 0.180948384403344 | 0.61129763161011 | 2.44519052644044 | 2.23062539809516 | 0.289740892106667 | 0.410227046634536 | 0.205625473761465 | 0.205625473761465 | 6.60510904180445 | 0.577876457579155 | 0.0213932568600168 | 0.0441250885084039 | 0 | 1 | 1 | 5.71009419059102 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.091946271550376 0.4899538991265 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.04459 | -13.376 | 33622414.0786135 | -1769875.01209835 | -17030025.791 | 6986617.478 | 6.9866 | 11 | 52.3175
gen_1085_2 | 51972235.2538258 | 11000 | 50 | 1300 | 4 | 0 | 0.180439341512765 | 0.596786349874875 | 2.3871453994995 | 2.22495364837607 | 0.287777392736636 | 0.399492474041297 | 0.212849698951375 | 0.212849698951375 | 6.42466781241242 | 0.557730817954428 | 0.0210970202903962 | 0.0440704936427763 | 0 | 1 | 1 | 5.68853632065933 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0905377852313686 0.491680710509419 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.04206 | -13.1227 | 34037052.0007346 | -2423787.4515906 | -17677017.947 | 7617062.496 | 7.6171 | 11 | 51.9722
gen_2003_7 | 86468466.58103171 | 13800.0 | 50 | 1300 | 4 | 0 | 0.07037058142991739 | 0.3368692087645175 | 1.34747683505807 | 0.692169924931601 | 0.19645158962626 | 0.140459885574644 | 0.140459885574644 | 10 | 13.1152812681953 | 0.257573597604642 | 0.08006743506900969 | 0.01 | 0 | 1 | 1 | 5.47055249727331 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0728272421874572 0.151229159968207 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97085 | 34.3908 | 64583504.1874736 | 374628.206080198 | -29313641.3497958 | 32339815.942443 | 32.3398 | 13.8 | 86.4685
gen_2004_8 | 90033975.4913002 | 13800.0 | 50 | 1300 | 4 | 0 | 0.0703134508477524 | 0.33792818401591 | 1.35171273606364 | 0.689755036254413 | 0.194228103008587 | 0.140206874543801 | 0.140206874543801 | 10 | 12.9697125383955 | 0.259286031714873 | 0.08258637520298361 | 0.01 | 0 | 1 | 1 | 5.44570927568246 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.07119631454139019 0.156920705217635 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9712 | 34.1715 | 58695544.7667194 | 366359.938384267 | -30050458.8578418 | 31177640.7402344 | 31.1776 | 13.8 | 90.034
gen_2010_1 | 98958854.7302624 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.15170433190302 | 0.29580283292412 | 1.18321133169648 | 0.599022037639283 | 0.284851787428372 | 0.190709760872647 | 0.190709760872647 | 10 | 9.401682886714109 | 0.150723496227292 | 0.0541547991681844 | 0.01 | 0 | 1 | 1 | 3.99037735044956 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.13186093249172 0.582683173609432 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.06431 | 39.5155 | 50990623.1932343 | -3249803.09639736 | -4017584.09256649 | 4110307.38369925 | 4.1103 | 0.69 | 98.9589
gen_2011_2 | 179468505.843356 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.154250349970534 | 0.2913376410931825 | 1.16535056437273 | 0.599254368624184 | 0.281819752996787 | 0.193881744362647 | 0.193881744362647 | 10 | 9.400862963497641 | 0.152091597591061 | 0.0520561677645892 | 0.01 | 0 | 1 | 1 | 4.08250164640555 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.134941022572108 0.598012115219142 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.05968 | 42.774 | 112974040.279931 | -3936281.0441209 | -4413120.23916012 | 4332451.26562393 | 4.3325 | 0.69 | 179.4685
gen_2012_1 | 23387192.14 | 11000 | 50 | 1300 | 4 | 0 | 0.124883695847355 | 0.2266249050199985 | 0.906499620079994 | 0.613079078556038 | 0.174670651662163 | 0.15064032941591 | 0.15064032941591 | 10 | 9.70420996861067 | 0.10216426093597 | 0.0582677543990125 | 0.01 | 0 | 1 | 1 | 2.46005736810854 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9771300000000001 | 27.7249 | 12718660.3319786 | 3066131.13418235 | 0 | 6315259.54473764 | 6.3153 | 11 | 23.3872
gen_2014_1 | 189475386.2 | 15500.0 | 50 | 1300 | 4 | 0 | 0.154798019940499 | 0.3756812654261 | 1.5027250617044 | 0.8524309190064669 | 0.204563326168433 | 0.192903413359774 | 0.192903413359774 | 10 | 9.141628227840179 | 0.162205352655728 | 0.0614735024808906 | 0.01 | 0 | 1 | 1 | 4.06409697877243 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97456 | 32.9009 | 165978187.592202 | 343592.807862908 | -43796791.9344082 | 78808096.01417281 | 78.8081 | 15.5 | 189.4754
gen_2015_1 | 70265223.5693065 | 11000 | 50 | 1300 | 4 | 0 | 0.157253336323192 | 0.29060807755409 | 1.16243231021636 | 0.657546600654721 | 0.303909980649501 | 0.180059996055462 | 0.180059996055462 | 10 | 5.75818576203892 | 0.125639858629312 | 0.0584789610555745 | 0.01 | 0 | 1 | 1 | 4.7044058326981 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00988 | 27.7775 | 51463473.9701658 | -11530151.942175 | -25215766.8292522 | 31244932.9170631 | 31.2449 | 11 | 70.2652
gen_2016_2 | 71079563.29288891 | 11000 | 50 | 1300 | 4 | 0 | 0.153311754179886 | 0.28831481979828 | 1.15325927919312 | 0.646937878787518 | 0.308310711539956 | 0.183554414698621 | 0.183554414698621 | 10 | 5.59510483304039 | 0.129609208103679 | 0.0599073628931656 | 0.01 | 0 | 1 | 1 | 4.5725358363823 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.0122 | 27.9937 | 53788216.4716721 | -9824559.24073085 | -25404623.4145761 | 31741274.535656 | 31.7413 | 11 | 71.0796
gen_2021_14 | 152586644.802825 | 17000 | 50 | 1300 | 4 | 0 | 0.149407079946063 | 0.339148916915 | 1.35659566766 | 0.718284736941568 | 0.272417223002063 | 0.184559151216224 | 0.184559151216224 | 10 | 9.649573004084081 | 0.204975472120568 | 0.063479751940188 | 0.01 | 0 | 1 | 1 | 3.7471230134205 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.95996 | 27.1121 | 115279070.18157 | -15398137.6222435 | -49018481.1728541 | 48379073.5420771 | 48.3791 | 17 | 152.5866
gen_2024_2 | 108100446.894949 | 15000 | 50 | 1300 | 4 | 0 | 0.140207213005051 | 0.276688239189155 | 1.10675295675662 | 0.661138976527005 | 0.277829190868651 | 0.257079988287389 | 0.257079988287389 | 10 | 8.644294168148191 | 0.207557347007096 | 0.0467904670265503 | 0.01 | 0 | 1 | 1 | 3.70091583372094 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0283119901584461 0.172946158540947 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.96635 | 25.8987 | 69712133.3398338 | -6704210.66225446 | -41160149.9140263 | 41742438.9316002 | 41.7424 | 15 | 108.1004
gen_2028_6 | 110470307.527771 | 15000 | 50 | 1300 | 4 | 0 | 0.141533667792915 | 0.283993088279735 | 1.13597235311894 | 0.651046621859539 | 0.271353758693906 | 0.261211925436929 | 0.261211925436929 | 10 | 8.5900621545501 | 0.203371186354198 | 0.0479352800024208 | 0.01 | 0 | 1 | 1 | 3.72723273860291 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0283815097064711 0.176099767547892 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97242 | 25.8058 | 65804614.318345 | -900903.784301877 | -41280738.2822037 | 42260004.3794839 | 42.26 | 15 | 110.4703
gen_2030_8 | 108179150.129217 | 15000 | 50 | 1300 | 4 | 0 | 0.137732337652124 | 0.288221267361905 | 1.15288506944762 | 0.639310903342487 | 0.270161778015085 | 0.256180270528141 | 0.256180270528141 | 10 | 8.85834268579492 | 0.204495833693072 | 0.0482526364274789 | 0.01 | 0 | 1 | 1 | 3.64607256987132 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0293098239625804 0.172572864756896 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.96361 | 25.9085 | 69538675.56027991 | -9849163.054861689 | -41143505.42631 | 42237306.916737 | 42.2373 | 15 | 108.1792
gen_2036_1 | 107325694.307219 | 10500.0 | 50 | 1300 | 4 | 0 | 0.125024369685911 | 0.43566993067311 | 1.74267972269244 | 1.71331186818467 | 0.240637742372719 | 0.278220606380375 | 0.15050190007803 | 0.15050190007803 | 5.62580722622946 | 1.41292391285859 | 0.0377539766477421 | 0.0522054060432129 | 0 | 1 | 1 | 9.08808681561146 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.95738 | 40.7061 | 71383955.40873471 | 2326386.27378177 | -32341330.6355942 | 39695614.01579989 | 39.6956 | 10.5 | 107.3257
gen_2037_2 | 107571180.567611 | 10500.0 | 50 | 1300 | 4 | 0 | 0.12429026450403 | 0.4411855168432475 | 1.76474206737299 | 1.70471853161333 | 0.234873122577253 | 0.271363207275979 | 0.148858594405348 | 0.148858594405348 | 5.63324014986213 | 1.42386981241591 | 0.0373273120949976 | 0.0513340991328005 | 0 | 1 | 1 | 9.01305640603649 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.93803 | 41.0086 | 72452673.30743369 | -12012861.7628943 | -32419386.3307592 | 40019604.6266938 | 40.0196 | 10.5 | 107.5712
gen_2038_3 | 108142809.283454 | 10500.0 | 50 | 1300 | 4 | 0 | 0.121093014190905 | 0.43690150760049 | 1.74760603040196 | 1.67854669901873 | 0.241891812811024 | 0.281901037345408 | 0.157927029657736 | 0.157927029657736 | 5.56171743093361 | 1.66273468548339 | 0.0322230394623708 | 0.287701905578258 | 0 | 1 | 1 | 9.0093198225135 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.94763 | 40.9637 | 71406951.50757751 | -4670460.6956616 | -31640905.901324 | 39248258.9823194 | 39.2483 | 10.5 | 108.1428
gen_2040_1 | 201368655.754533 | 15750.00 | 50 | 1300 | 4 | 0 | 0.147430063947011 | 0.56852672272101 | 2.27410689088404 | 2.13640583073918 | 0.2405936365854 | 0.628676544888876 | 0.179588804137288 | 0.179588804137288 | 12.1670928301318 | 1.92622005773117 | 0.0458926945318468 | 0.210096588095012 | 0 | 1 | 1 | 6.14963329207208 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.213149927735503 0.876194069808419 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98898 | 30.6286 | 136046296.661597 | -7368156.47080434 | -30281606.6885351 | 100402186.952972 | 100.4022 | 15.75 | 201.3687
gen_2041_2 | 201766158.744693 | 15750.00 | 50 | 1300 | 4 | 0 | 0.14895520463041 | 0.566038564199955 | 2.26415425679982 | 2.08898139820669 | 0.24397955252789 | 0.60955103523354 | 0.184987030366622 | 0.184987030366622 | 12.2804884779193 | 1.91468615333024 | 0.0445534495728929 | 0.20304874447389 | 0 | 1 | 1 | 6.14581909604918 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.211620692036231 0.879657702257987 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99603 | 30.488 | 143326529.05182 | -2030177.69778478 | -30145730.1235249 | 101370253.659187 | 101.3703 | 15.75 | 201.7662
gen_2043_2 | 630752565.958723 | 24000 | 50 | 1300 | 4 | 0 | 0.238656334180152 | 0.7660784252341825 | 3.06431370093673 | 1.97162422098429 | 0.322901312890928 | 0.562876404516865 | 0.282570772883482 | 0.282570772883482 | 8.078392870917449 | 1.6656421950832 | 0.0257566751906415 | 0.0609874658533372 | 0 | 1 | 1 | 4.74471527724992 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0620794791110791 0.566092940667551 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00618 | 37.1328 | 346950054.543794 | -36692059.4819474 | -207056388.105103 | 320623920.853133 | 320.6239 | 24 | 630.7526
gen_2044_3 | 692476477.046125 | 21000 | 50 | 1300 | 4 | 0 | 0.100007683518343 | 0.7142032438178725 | 2.85681297527149 | 1.75351179362624 | 0.233962958633783 | 0.717366185103077 | 0.209143309472781 | 0.209143309472781 | 9.63119054253213 | 1.06803487882367 | 0.0360135997417383 | 0.123079596955329 | 0 | 1 | 1 | 3.12175265106224 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.128958338149451 0.411295651755529 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01171 | 39.203 | 545601412.348538 | 6578139.15332565 | -196662271.597704 | 306758432.27841 | 306.7584 | 21 | 692.4765
gen_2045_4 | 743727576.350409 | 21000 | 50 | 1300 | 4 | 0 | 0.16241376766935 | 0.726353932854755 | 2.90541573141902 | 2.71512390831774 | 0.344685269669304 | 0.802516619203077 | 0.254124888244318 | 0.254124888244318 | 9.618236888374669 | 2.62273582036141 | 0.0404989788755775 | 0.153707704602275 | 0 | 1 | 1 | 3.50812415473688 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.143703583321068 0.583817961183004 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9903 | 39.1056 | 526740899.209748 | -74916316.0444217 | -100123241.56 | 333469650 | 333.4697 | 21 | 743.7276
gen_2046_1 | 651183072.42021 | 20000 | 50 | 1300 | 4 | 0 | 0.220370596198132 | 0.69228188475984 | 2.76912753903936 | 1.49396912607029 | 0.292980902360985 | 0.902106047159061 | 0.27078077274668 | 0.27078077274668 | 7.9957560302061 | 0.878809587816941 | 0.0354125640279381 | 0.113304608154576 | 0 | 1 | 1 | 2.82492999458686 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.110870278429007 0.5287843568409329 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99891 | 39.544 | 511886080.085132 | 55344790.2990598 | -108032944.965043 | 321508501.711393 | 321.5085 | 20 | 651.1831
gen_2047_2 | 647149878.913164 | 20000 | 50 | 1300 | 4 | 0 | 0.21672931684088 | 0.6795054174677225 | 2.71802166987089 | 1.53402564272303 | 0.291363623245386 | 0.92106840505451 | 0.272641338658379 | 0.272641338658379 | 7.98948127645068 | 0.8879521721950731 | 0.0358368078892818 | 0.113771175741684 | 0 | 1 | 1 | 2.89715258527547 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.11333135988703 0.524200491215428 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99686 | 39.749 | 529759362.199972 | 47884664.7386803 | -104661043.576273 | 323341019.248349 | 323.341 | 20 | 647.1499
gen_2054_1 | 115622949.829081 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.153062255956465 | 0.296177483896085 | 1.18470993558434 | 0.596343371211085 | 0.288383334587328 | 0.190769310319214 | 0.190769310319214 | 10 | 9.16600971654989 | 0.154421589545673 | 0.0544922863943502 | 0.01 | 0 | 1 | 1 | 4.03117492500646 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.130411274833372 0.59412612610124 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.06524 | 45.1778 | 90018906.37953861 | 4446300.64787595 | -4993100.70382631 | 4885382.507806361 | 4.8854 | 0.69 | 115.6229
gen_2055_2 | 69650679.63275069 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.150796227111714 | 0.295218588298245 | 1.18087435319298 | 0.603036889829207 | 0.284297608871013 | 0.18842873855005 | 0.18842873855005 | 10 | 9.07309239946771 | 0.15207743184641 | 0.0544717363826931 | 0.01 | 0 | 1 | 1 | 4.06066666295053 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.133343112369068 0.594565711029805 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.07291 | 44.8269 | 51775591.3180758 | 9890281.195852911 | -26051903.25 | 15976388.8 | 15.9764 | 0.69 | 69.6507
gen_2056_3 | 46581592.120633 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.157472956760321 | 0.28895081533835 | 1.1558032613534 | 0.59405834513763 | 0.287780083508231 | 0.185772904127254 | 0.185772904127254 | 10 | 9.02770271510817 | 0.151836432883283 | 0.053185727585014 | 0.01 | 0 | 1 | 1 | 4.08431555336993 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.136108512234408 0.581609428610653 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.07773 | 45.0306 | 27502320.5825697 | 7647129.22532787 | -7902615.13235117 | 7813163.267061421 | 7.8132 | 0.69 | 46.5816
gen_2057_4 | 114864380.666002 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.155206665890291 | 0.289167836851905 | 1.15667134740762 | 0.6073674085112289 | 0.292207703014836 | 0.187924511490506 | 0.187924511490506 | 10 | 9.358395589026619 | 0.155718487343984 | 0.0534328781481832 | 0.01 | 0 | 1 | 1 | 4.02206549641024 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.134532691539265 0.607950304671656 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.07461 | 41.804 | 50684187.9442334 | 9829859.492392281 | -12087261.8720163 | 11791324.23804 | 11.7913 | 0.69 | 114.8644
gen_2058_5 | 73235160.54158161 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.156863717761589 | 0.2938788464727125 | 1.17551538589085 | 0.595197321349289 | 0.284556783134118 | 0.186409482990741 | 0.186409482990741 | 10 | 9.02192411413416 | 0.151637689943891 | 0.0524561489649117 | 0.01 | 0 | 1 | 1 | 3.99848786202748 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.134033706157934 0.602461138121318 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.07694 | 42.1318 | 30970484.6722931 | 6608656.17792485 | -7434656.45323303 | 7276915.77513651 | 7.2769 | 0.69 | 73.2352
gen_2059_6 | 113018319.971292 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.15744628916611 | 0.2832616046133325 | 1.13304641845333 | 0.597387936248444 | 0.287029509564862 | 0.185813261497533 | 0.185813261497533 | 10 | 9.35010723690502 | 0.156428222410614 | 0.0537023312235251 | 0.01 | 0 | 1 | 1 | 3.9632122449968 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.134673681959277 0.602642043429892 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.08353 | 43.6049 | 43348984.2760144 | 8974411.675248342 | -24384855.461 | 14532299.273 | 14.5323 | 0.69 | 113.0183
gen_2060_1 | 100974593 | 11500.0 | 50 | 1300 | 4 | 0 | 0.129965120342835 | 0.3770897290089975 | 1.50835891603599 | 0.824091705071489 | 0.387085386070171 | 0.217732234889237 | 0.217732234889237 | 10 | 7.68085595152594 | 0.084247076077899 | 0.0698387765660137 | 0.01 | 0 | 1 | 1 | 3.30043171584606 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.128144556057127 0.707332838140894 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97517 | 32.0107 | 50769790.687559 | -870072.425790271 | -13642655.9246816 | 16823914.9765134 | 16.8239 | 11.5 | 100.9746
gen_2061_5 | 100364584.8 | 11500.0 | 50 | 1300 | 4 | 0 | 0.12580229607692 | 0.377666472370025 | 1.5106658894801 | 0.845341116429898 | 0.403676320665549 | 0.222751605621412 | 0.222751605621412 | 10 | 7.58959724868929 | 0.08189537336241449 | 0.0729844010128453 | 0.01 | 0 | 1 | 1 | 3.34387728109956 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.129885810557031 0.7042550601650031 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97542 | 31.8142 | 46912125.0839084 | -886707.020449638 | -13476504.6079771 | 16133660.0902486 | 16.1337 | 11.5 | 100.3646
gen_2062_2 | 100148673 | 11500.0 | 50 | 1300 | 4 | 0 | 0.128620932018664 | 0.376256542097455 | 1.50502616838982 | 0.83213562498488 | 0.392660750422804 | 0.220365055460222 | 0.220365055460222 | 10 | 7.50128685525794 | 0.08204095216181601 | 0.070840064334143 | 0.01 | 0 | 1 | 1 | 3.21453293256462 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.127854901388474 0.703062873454392 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97015 | 32.1768 | 49475084.3232734 | -909071.200627182 | -13842234.1934865 | 16553983.1709787 | 16.554 | 11.5 | 100.1487
gen_2063_11 | 352297983.41787 | 20000 | 50 | 1300 | 4 | 0 | 0.191272909612942 | 0.558759305460845 | 2.23503722184338 | 1.80545373802611 | 0.247864859093418 | 0.43446545309342 | 0.20616501327022 | 0.20616501327022 | 14.7992703462001 | 1.66678917597644 | 0.0740629145089071 | 0.0785728729372844 | 0 | 1 | 1 | 6.1948830040202 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.131922701058844 0.750702290336019 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99413 | 37.3628 | 259780769.472675 | 29380438.9431105 | -67068610.7195914 | 125995531.298965 | 125.9955 | 20 | 352.298
gen_2064_12 | 353577216.341277 | 20000 | 50 | 1300 | 4 | 0 | 0.198265866280301 | 0.571760032062045 | 2.28704012824818 | 1.81476633016775 | 0.250246868084436 | 0.417571711633354 | 0.206042246815632 | 0.206042246815632 | 14.7433220908174 | 1.7203412002414 | 0.07488318341528059 | 0.0770717675060965 | 0 | 1 | 1 | 6.25485634361487 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.127360670649963 0.677196917318972 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.989 | 37.1611 | 247874550.00916 | 16770819.4425677 | -66745078.77631111 | 125559830.033267 | 125.5598 | 20 | 353.5772
gen_2069_1 | 51611933.0540299 | 11000 | 50 | 1300 | 4 | 0 | 0.132047091756854 | 0.428086248115695 | 1.71234499246278 | 1.67432753258985 | 0.24952969160839 | 0.400432061496796 | 0.196355714112404 | 0.196355714112404 | 6.107127386868 | 0.449100501766196 | 0.0388881832155399 | 0.0592212326824199 | 0 | 1 | 1 | 2.09427953171544 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.133330417062622 0.506281487579481 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99081 | 44.2378 | 31694694.6251169 | -3305417.75477491 | -14247713.5847208 | 23848436.9408552 | 23.8484 | 11 | 51.6119
gen_2073_1 | 626956900.197733 | 24000 | 50 | 1300 | 4 | 0 | 0.232123611525167 | 0.787430443246615 | 3.14972177298646 | 1.89472809397336 | 0.312551544700051 | 0.571152368282201 | 0.282732842341997 | 0.282732842341997 | 8.042133202410771 | 1.63130434907973 | 0.0252934310870478 | 0.0606394733847119 | 0 | 1 | 1 | 4.78634356811922 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0646734404373448 0.5777143036279599 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9662500000000001 | 31.0039 | 473373842.322757 | 45658055.0539587 | -169321169.144879 | 257205845.451355 | 257.2058 | 24 | 626.9569
gen_2091_1 | 100808734.6 | 11500.0 | 50 | 1300 | 4 | 0 | 0.119260698258248 | 0.2485487533537845 | 0.9941950134151381 | 0.6155278328632 | 0.319939966568956 | 0.208017124790722 | 0.208017124790722 | 10 | 8.44111767042777 | 0.0856915255014785 | 0.0314025864723837 | 0.01 | 0 | 1 | 1 | 4.47370711159601 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97029 | 28.3093 | 28837604.2157381 | -3449325.37813294 | -13187919.2154855 | 15784886.6862478 | 15.7849 | 11.5 | 100.8087
gen_2092_1 | 476643849.198753 | 20000 | 50 | 1300 | 4 | 0 | 0.176396053616796 | 0.511766669164295 | 2.04706667665718 | 1.97365733031929 | 0.271743498196453 | 0.225107598190312 | 0.225107598190312 | 10 | 7.3165585881006 | 0.272367673363467 | 0.0380721040721284 | 0.01 | 0 | 1 | 1 | 3.33360681051202 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.99185 | 41.0256 | 348993836.114038 | -78075644.14404921 | -118968445.812119 | 180333202.431328 | 180.3332 | 20 | 476.6438
gen_2093_2 | 413478915.313189 | 20000 | 50 | 1300 | 4 | 0 | 0.17255781546915 | 0.5006249842629775 | 2.00249993705191 | 1.99729462185502 | 0.271790645513311 | 0.21634164256847 | 0.21634164256847 | 10 | 7.31055407261476 | 0.270961899555149 | 0.0370197912551463 | 0.01 | 0 | 1 | 1 | 3.28558189037256 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9728599999999999 | 33.1572 | 315804972.445372 | -44229590.3584657 | -117951626.536436 | 185486093.439604 | 185.4861 | 20 | 413.4789
gen_2094_3 | 481327456.929814 | 20000 | 50 | 1300 | 4 | 0 | 0.21278581263274 | 0.618070858482155 | 2.47228343392862 | 2.37412631153595 | 0.316171454609558 | 0.269446662588138 | 0.269446662588138 | 10 | 8.1800689175725 | 0.0703483978975564 | 0.0405651944782585 | 0.01 | 0 | 1 | 1 | 2.84203912114631 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9922299999999999 | 32.7139 | 326010094.955155 | 13788899.8626748 | -144214756.964589 | 192905989.068886 | 192.906 | 20 | 481.3275
gen_2095_4 | 475496667.556395 | 20000 | 50 | 1300 | 4 | 0 | 0.165382165543782 | 0.5659252276341425 | 2.26370091053657 | 2.06833851886913 | 0.281499481397169 | 0.20535805297941 | 0.20535805297941 | 10 | 9.01403412369709 | 0.304586769940252 | 0.0405587120503187 | 0.01 | 0 | 1 | 1 | 3.07100263712928 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 2 | 2 | [0 0 0 0 0 0 0 0 0 0] | [1 1.2 0 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98956 | 33.5195 | 384301297.50208 | 11433909.8354056 | -144348324.105609 | 193607759.779878 | 193.6078 | 20 | 475.4967
gen_2322_3 | 47133886.6906008 | 10500.0 | 50 | 1300 | 4 | 0 | 0.135614820701117 | 0.61594825312954 | 2.46379301251816 | 1.80323555976357 | 0.255631518942537 | 0.410739804014389 | 0.160890100223757 | 0.160890100223757 | 4.45158014260149 | 0.37324356560007 | 0.021248307089248 | 0.06339402748252961 | 0 | 1 | 1 | 6.17647337724431 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0773319850559346 0.323849116496742 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02644 | 25.8829 | 34370872.62522779 | 1001412.80425424 | -12860151.2594149 | 19351623.0660025 | 19.3516 | 10.5 | 47.1339
gen_2323_4 | 46128338.4356648 | 10500.0 | 50 | 1300 | 4 | 0 | 0.134278066840326 | 0.62873387726635 | 2.5149355090654 | 1.79202628061157 | 0.255641689372133 | 0.415280793136258 | 0.159617642189702 | 0.159617642189702 | 4.45641638381762 | 0.384897612011186 | 0.0208416807888779 | 0.0643816046734122 | 0 | 1 | 1 | 6.15002819432421 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0767526683356846 0.328133545421064 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02602 | 25.4584 | 32557922.5848377 | 666687.572085578 | -12972653.7105627 | 19507535.4155153 | 19.5075 | 10.5 | 46.1283
gen_2324_1 | 53539829.1399539 | 10500.0 | 50 | 1300 | 4 | 0 | 0.149059200884472 | 0.68280919779418 | 2.73123679117672 | 2.48358281386271 | 0.271188627389779 | 0.158051589153758 | 0.156744940988242 | 0.156744940988242 | 5.56300846283417 | 0.811437354814904 | 0.042133739922672 | 0.08705920038176231 | 0 | 1 | 1 | 5.25764129845053 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0797420477679931 0.334629224643111 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02719 | 25.3531 | 34989074.655062 | 894454.3812100771 | -16054868.7966354 | 19822111.973376 | 19.8221 | 10.5 | 53.5398
gen_2325_2 | 66537869.1187571 | 10500.0 | 50 | 1300 | 4 | 0 | 0.198655885283835 | 0.9024392279982675 | 3.60975691199307 | 2.67657415372133 | 0.369004891169176 | 0.236381660297401 | 0.227904606739432 | 0.227904606739432 | 5.49128959307652 | 0.598409325595759 | 0.0388154977258481 | 0.108059357956569 | 0 | 1 | 1 | 4.26221469973587 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0768497418945655 0.328209669783711 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.02592 | 25.0078 | 33002271.7441131 | 408944.916197751 | -13006189.1622841 | 19761341.5580941 | 19.7613 | 10.5 | 66.5379
gen_3154_3 | 56482992.7750938 | 11000 | 50 | 1300 | 4 | 0 | 0.100625005390029 | 0.3718171642226625 | 1.48726865689065 | 0.653736277539516 | 0.236309943563933 | 0.165369049217552 | 0.165369049217552 | 10 | 6.01524441617657 | 0.136285069723614 | 0.0409194248579442 | 0.01 | 0 | 1 | 1 | 6.02022996824328 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.15043238382088 0.424900714945514 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.99783 | 50.4819 | 38150068.13653801 | -1787086.23269442 | -18611840.6733032 | 29551508.5583902 | 29.5515 | 11 | 56.483
gen_3155_1 | 70401088.7629353 | 11000 | 50 | 1300 | 4 | 0 | 0.0936156283468008 | 0.5263130529960151 | 2.10525221198406 | 0.670176763130911 | 0.248329524861369 | 0.190548348950408 | 0.190548348950408 | 10 | 5.23850024223793 | 0.0372836178079247 | 0.0311510650548153 | 0.01 | 0 | 1 | 1 | 3.60993799746037 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.193288791911094 0.9991211643911661 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.0006 | 52.4612 | 54788962.4938389 | 188969.746815553 | -19541021.7327923 | 39445308.756288 | 39.4453 | 11 | 70.4011
gen_3156_2 | 55849572.7342218 | 11000 | 50 | 1300 | 4 | 0 | 0.100444898027927 | 0.3816853033265675 | 1.52674121330627 | 0.644433860891126 | 0.23943890593769 | 0.163149734124541 | 0.163149734124541 | 10 | 5.90473576803925 | 0.136108365259133 | 0.0414171042172238 | 0.01 | 0 | 1 | 1 | 5.93844899515156 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.137111357472371 0.404672492164746 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.97188 | 45.4918 | 37385241.6237806 | -2253410.38367646 | -19681359.9202316 | 40159007.5342683 | 40.159 | 11 | 55.8496
gen_3264_1 | 240121851.232834 | 15000 | 50 | 1300 | 4 | 0 | 0.178184038713109 | 0.615674319156795 | 2.46269727662718 | 2.38781679937579 | 0.250429041439458 | 0.422410171864554 | 0.195174052917492 | 0.195174052917492 | 10.4247302248478 | 0.918850534861675 | 0.021265989656467 | 0.0325859198257327 | 0 | 1 | 1 | 6.63361655944912 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.08939795621950181 0.473065880312119 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.05379 | 64.66249999999999 | 158622483.443077 | 10879602.3745763 | -16042929.7403083 | 18392053.9760521 | 18.3921 | 15 | 240.1219
gen_3295_1 | 989914190.588519 | 21000 | 50 | 1300 | 4 | 0 | 0.199349076014333 | 0.7230897461436875 | 2.89235898457475 | 2.72520976324555 | 0.327267125567719 | 1.09732162832391 | 0.209308132514635 | 0.209308132514635 | 6.49822890136416 | 2.09722201965679 | 0.0349455311762402 | 0.24632794285465 | 0 | 1 | 1 | 2.40391258200398 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.17525998005369 0.49884011385245 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.07483 | 56.0724 | 672011629.407089 | 11841863.4473528 | -210943182.773757 | 380783861.394891 | 380.7839 | 21 | 989.9142
gen_3301_1 | 47830978.4304584 | 66000 | 50 | 1300 | 4 | 0 | 0.142658731834032 | 0.5216690686102951 | 2.08667627444118 | 1.14978754612617 | 0.300747628742829 | 0.203913950338028 | 0.203913950338028 | 10 | 11.7666526484396 | 0.134077290374553 | 0.0403545063221827 | 0.01 | 0 | 1 | 1 | 2.70277349474677 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.07104306664131579 0.258720623917179 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00241 | 46.1648 | 32325133.0143116 | 3763016.86895667 | -16413106.9646683 | 16038295.2337386 | 16.0383 | 66 | 47.831
gen_3417_1 | 327941066.311374 | 15750.00 | 50 | 1300 | 4 | 0 | 0.18968452615547 | 0.5542875514127075 | 2.21715020565083 | 1.41951625270746 | 0.316110383726307 | 0.787180420593359 | 0.237618300461792 | 0.237618300461792 | 8.841047646263609 | 1.41977305095177 | 0.0355467345670331 | 0.134924549088813 | 0 | 1 | 1 | 3.86626404018374 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0944042776855384 0.341244472153904 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00238 | 65.05159999999999 | 233797681.069169 | 15388958.5213543 | -39163123.4456237 | 143431122.585477 | 143.4311 | 15.75 | 327.9411
gen_3418_2 | 328221132.472344 | 15750.00 | 50 | 1300 | 4 | 0 | 0.187139095534687 | 0.5441811000095925 | 2.17672440003837 | 1.42679221200664 | 0.323964714750415 | 0.756816770962905 | 0.240845218756702 | 0.240845218756702 | 8.945346971706019 | 1.42720811647829 | 0.0365770018170588 | 0.134260131702991 | 0 | 1 | 1 | 3.820521598591 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09130882321532351 0.344133747342508 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01725 | 64.14870000000001 | 228995223.334108 | 18305990.7175563 | -47780816.282485 | 143201212.325564 | 143.2012 | 15.75 | 328.2211
gen_3419_3 | 333526844.753549 | 15750.00 | 50 | 1300 | 4 | 0 | 0.188146094688028 | 0.5382673037995125 | 2.15306921519805 | 1.43418260413315 | 0.329564754615189 | 0.756886540021514 | 0.237310461413464 | 0.237310461413464 | 9.011984201988669 | 1.42844083372038 | 0.035481092891423 | 0.133668741711881 | 0 | 1 | 1 | 3.70773104398279 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0920463975860691 0.354161911594402 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.0801 | 60.5688 | 181826398.928217 | 2929921.44144773 | -60670346.03693061 | 146550946.039439 | 146.5509 | 15.75 | 333.5268
gen_3420_4 | 335174992.911071 | 15750.00 | 50 | 1300 | 4 | 0 | 0.189250415644329 | 0.5501170843886199 | 2.20046833755448 | 1.45560889990954 | 0.315368204015424 | 0.775654590973863 | 0.243262402186636 | 0.243262402186636 | 8.822544645974411 | 1.46002057570033 | 0.0354735213819658 | 0.130525620050728 | 0 | 1 | 1 | 3.7787187784072 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0921633735830476 0.350613086293964 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.07699 | 60.9899 | 193427735.065703 | 20864884.1696903 | -54823367.15865619 | 142575249.858822 | 142.5752 | 15.75 | 335.175
gen_3421_5 | 323952838.555873 | 15750.00 | 50 | 1300 | 4 | 0 | 0.189813048525085 | 0.5584359856872475 | 2.23374394274899 | 1.44029444648721 | 0.329721502720378 | 0.756618822208838 | 0.244184825941338 | 0.244184825941338 | 9.00120812370675 | 1.42893853170797 | 0.0353049714509398 | 0.136436433299445 | 0 | 1 | 1 | 3.74056686070515 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0925870090375864 0.346753837848036 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01396 | 61.8337 | 143623418.079618 | 8577015.2216617 | -82922326.2770218 | 145388036.156339 | 145.388 | 15.75 | 323.9528
gen_3422_6 | 321767278.076075 | 15750.00 | 50 | 1300 | 4 | 0 | 0.18743372169754 | 0.5410429907657101 | 2.16417196306284 | 1.4382248303974 | 0.321553241912043 | 0.755177663953509 | 0.239014847423183 | 0.239014847423183 | 9.070795653609091 | 1.46636158179026 | 0.0360380109102698 | 0.135713061690563 | 0 | 1 | 1 | 3.75828660446685 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0946230090580741 0.33824450410502 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01738 | 65.2957 | 252815251.121725 | 20528892.1560526 | -71682896.6359228 | 143540259.748406 | 143.5403 | 15.75 | 321.7673
gen_3423_1 | 422530060.780491 | 20000 | 50 | 1300 | 4 | 0 | 0.271956206222065 | 0.58663344774302 | 2.34653379097208 | 2.38811071860604 | 0.374671747592278 | 0.615954936782364 | 0.313211768131238 | 0.313211768131238 | 6.97784928334411 | 1.03591020514723 | 0.0472164834095165 | 0.0680591719527729 | 0 | 1 | 1 | 2.71856869414169 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09498108428199779 0.29471710016448 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01525 | 50.4041 | 339366602.367447 | 9450693.26332528 | -91574557.6726452 | 179942936.235107 | 179.9429 | 20 | 422.5301
gen_3424_2 | 422440994.499065 | 20000 | 50 | 1300 | 4 | 0 | 0.268802522245329 | 0.6021013914016075 | 2.40840556560643 | 2.38183231748082 | 0.360658929898404 | 0.6238518974469039 | 0.310896574940067 | 0.310896574940067 | 6.99216537688626 | 1.01008997280151 | 0.0456134201057721 | 0.0680016349351034 | 0 | 1 | 1 | 2.69100713427644 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09431959676947441 0.300689465802796 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01123 | 50.7401 | 328650323.317071 | 1834370.86554319 | -92373041.45073789 | 181872876.888374 | 181.8729 | 20 | 422.441
gen_3425_3 | 416575441.945856 | 20000 | 50 | 1300 | 4 | 0 | 0.262291630129796 | 0.58602766990196 | 2.34411067960784 | 2.3776905409731 | 0.36178484119568 | 0.624340658576926 | 0.314381588094635 | 0.314381588094635 | 6.8380361740361 | 1.018040044792 | 0.0466622058417415 | 0.068566897973977 | 0 | 1 | 1 | 2.70601596333087 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09837848503375431 0.301908637393909 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01182 | 50.9817 | 333605957.972587 | 3307253.65806478 | -89721559.3289731 | 180996407.369385 | 180.9964 | 20 | 416.5754
gen_3426_4 | 411612221.374409 | 20000 | 50 | 1300 | 4 | 0 | 0.260394301671069 | 0.6006789432642975 | 2.40271577305719 | 2.37170177614689 | 0.364851457097568 | 0.6289099826193419 | 0.317155488227494 | 0.317155488227494 | 6.89142244027462 | 1.01466865255497 | 0.0470498466367135 | 0.07094914040844889 | 0 | 1 | 1 | 2.78368466207199 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.096046440549288 0.29969200202425 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01054 | 50.9876 | 352540245.030636 | 28110339.5883693 | -92679939.08473401 | 186845473.877853 | 186.8455 | 20 | 411.6122
gen_3430_1 | 428869098.612061 | 20000 | 50 | 1300 | 4 | 0 | 0.278994397855829 | 0.577217709455405 | 2.30887083782162 | 1.6773203096858 | 0.32652929502558 | 0.393120866359747 | 0.300744122507051 | 0.300744122507051 | 5.13921708392445 | 2.03895327723585 | 0.0281393186561996 | 0.239056875193492 | 0 | 1 | 1 | 2.74872787492443 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0982709180471487 0.301524968782146 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01726 | 72.6204 | 291083117.94627 | -1213972.36466594 | -106226863.863412 | 181356975.155417 | 181.357 | 20 | 428.8691
gen_3431_2 | 413432336.428249 | 20000 | 50 | 1300 | 4 | 0 | 0.277044602485257 | 0.57261486406764 | 2.29045945627056 | 1.75171339861888 | 0.325070057422668 | 0.406744629743905 | 0.299484664914687 | 0.299484664914687 | 5.21611048839986 | 2.08348544691689 | 0.027697838442307 | 0.238239405105589 | 0 | 1 | 1 | 2.72372304161079 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0971263587618247 0.290630471755229 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01886 | 73.52849999999999 | 337084054.74398 | 2372350.24599703 | -108683592.199814 | 180782998.914132 | 180.783 | 20 | 413.4323
gen_3434_1 | 158354711.054701 | 15000 | 50 | 1300 | 4 | 0 | 0.112458837043738 | 0.4354186370585825 | 1.74167454823433 | 1.63401958680067 | 0.243421422506694 | 0.676707782286685 | 0.182454745493736 | 0.182454745493736 | 9.62945421797982 | 1.59715483102575 | 0.0471132505866699 | 0.0756010422993917 | 0 | 1 | 1 | 7.10239334703865 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.159174129848718 0.875452109647449 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01934 | 51.8251 | 97701398.83497311 | 4294679.49318355 | -44005962.5754378 | 64713450.4035086 | 64.7135 | 15 | 158.3547
gen_3435_2 | 157839378.21052 | 15000 | 50 | 1300 | 4 | 0 | 0.113130421920586 | 0.4372074026148525 | 1.74882961045941 | 1.62910746678001 | 0.235475331413152 | 0.66835482379538 | 0.181810139138531 | 0.181810139138531 | 10.075610053159 | 1.62233106968924 | 0.0450799652872374 | 0.07645218429751691 | 0 | 1 | 1 | 6.96282623333484 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.16086052753916 0.77851692851237 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01637 | 51.7865 | 99968940.6776247 | 1159175.5747586 | -42916013.4657559 | 65640466.49780419 | 65.6405 | 15 | 157.8394
gen_3436_3 | 153609530.652668 | 15000 | 50 | 1300 | 4 | 0 | 0.112414862059581 | 0.427048611814845 | 1.70819444725938 | 1.68207166656596 | 0.232582163608365 | 0.667773232948966 | 0.183731930937944 | 0.183731930937944 | 10.5812228892087 | 1.64749556288123 | 0.0460557944513857 | 0.0757992805988761 | 0 | 1 | 1 | 6.94982702993392 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.139857704689354 0.694928226575279 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.009 | 51.9572 | 107519953.011375 | -6630803.83109897 | -43144307.8425118 | 65640340.41714611 | 65.6403 | 15 | 153.6095
gen_3437_4 | 375605614.145869 | 15000 | 50 | 1300 | 4 | 0 | 0.197573733603896 | 0.5656208392587025 | 2.26248335703481 | 2.24766059143685 | 0.33568448709901 | 0.566703780147931 | 0.260207124897318 | 0.260207124897318 | 7.41282163191959 | 0.554108337114216 | 0.0400270751188276 | 0.07693287145304489 | 0 | 1 | 1 | 3.14703987953276 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0786652872574516 0.489276197398547 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.06955 | 53.3166 | 254350826.058781 | 114025829.00407 | -84200625.01158379 | 154606299.471656 | 154.6063 | 15 | 375.6056
gen_3438_1 | 209356691.142824 | 15750.00 | 50 | 1300 | 4 | 0 | 0.143520517237941 | 0.6299167819390425 | 2.51966712775617 | 1.66677655987348 | 0.226013841770897 | 1.33642655266873 | 0.169378895296929 | 0.169378895296929 | 13.7501555766666 | 3.58677893648786 | 0.562812431588769 | 0.6233602077560501 | 0 | 1 | 1 | 6.01690277789254 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.192392512983382 0.749744022292865 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.96738 | 52.4306 | 133617273.394639 | 1669069.5347473 | -55428368.0641939 | 84253527.13164 | 84.2535 | 15.75 | 209.3567
gen_3439_2 | 205187497.459818 | 15750.00 | 50 | 1300 | 4 | 0 | 0.143617800862212 | 0.5840767539287325 | 2.33630701571493 | 1.73738662648201 | 0.223073005936742 | 1.35569246493266 | 0.173830290560033 | 0.173830290560033 | 13.5332678150258 | 3.572616360866 | 0.0561062996534631 | 0.6290303697572091 | 0 | 1 | 1 | 6.05484230023809 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.190450115207285 0.775795620411821 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.96634 | 53.6775 | 167280394.055444 | 3215774.74417374 | -50221432.574884 | 88203119.38069111 | 88.2031 | 15.75 | 205.1875
gen_3442_1 | 628052562.262723 | 19500.0 | 50 | 1300 | 4 | 0 | 0.229095244088396 | 0.4690290484931325 | 1.87611619397253 | 1.90396073045302 | 0.33761339498919 | 0.539150571256271 | 0.280788481080346 | 0.280788481080346 | 6.49123385105608 | 1.43420447916258 | 0.03498675205498 | 0.0407677942737937 | 0 | 1 | 1 | 3.01790625403007 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.127818385281716 0.44485959874437 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98831 | 71.9766 | 392371622.716256 | 15863500.4029665 | -113626588.569721 | 222015781.296394 | 222.0158 | 19.5 | 628.0526
gen_3443_2 | 638170104.924729 | 19500.0 | 50 | 1300 | 4 | 0 | 0.229082102052402 | 0.4808356375694275 | 1.92334255027771 | 1.94636825631536 | 0.348516051633307 | 0.531549231579946 | 0.272004663884919 | 0.272004663884919 | 6.36829916049261 | 1.46957646857947 | 0.0347444396400359 | 0.0406297421539202 | 0 | 1 | 1 | 3.0858770133506 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.131087403011043 0.447417936634156 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98849 | 71.9924 | 389173659.274105 | 16542018.9852119 | -111292102.674488 | 217955337.709421 | 217.9553 | 19.5 | 638.1701
gen_3444_1 | 671132690.536673 | 20500.0 | 50 | 1300 | 4 | 0 | 0.223891816075658 | 0.462616370117815 | 1.85046548047126 | 1.89170319255325 | 0.322514147432987 | 0.520653011214687 | 0.244371353888186 | 0.244371353888186 | 6.53116008633329 | 1.41699244437274 | 0.0360051458599046 | 0.0471268866275903 | 0 | 1 | 1 | 2.85345358852949 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.131461175711383 0.451748831035984 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.97748 | 51.3566 | 446095845.639464 | 33846533.7004101 | -208673075.855873 | 250306133.095035 | 250.3061 | 20.5 | 671.1327
gen_3448_1 | 35382485.4665436 | 11000 | 50 | 1300 | 4 | 0 | 0.126975880239205 | 0.356652551978605 | 1.42661020791442 | 0.8173371608082211 | 0.324694296703194 | 0.20019613171611 | 0.20019613171611 | 10 | 8.16106135559008 | 0.184429087537788 | 0.07114009471591561 | 0.01 | 0 | 1 | 1 | 2.43705472178757 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0906167020519232 0.263332975166002 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01974 | 34.1465 | 0 | 124195.797505276 | -12923632.0733093 | 16067047.7952808 | 16.067 | 11 | 35.3825
gen_3449_2 | 35106357.0457092 | 11000 | 50 | 1300 | 4 | 0 | 0.166865420665592 | 0.30697036185608 | 1.22788144742432 | 0.5403237317344169 | 0.285440440901094 | 0.221875491310218 | 0.221875491310218 | 10 | 6.78570924373809 | 0.160132405337552 | 0.0692698138938285 | 0.01 | 0 | 1 | 1 | 3.22817093857541 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.103165797910187 0.304445681607872 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.02374 | 39.1548 | 26060170.4499722 | -192852.384490659 | -12985960.8175233 | 16315765.9617718 | 16.3158 | 11 | 35.1064
gen_3453_1 | 24084150.3046104 | 11000 | 50 | 1300 | 4 | 0 | 0.137558170996606 | 0.2627915696300325 | 1.05116627852013 | 0.558998181402683 | 0.257704870495945 | 0.180433868899941 | 0.180433868899941 | 10 | 6.12672656222945 | 0.158503101532022 | 0.0562831844830886 | 0.01 | 0 | 1 | 1 | 2.96793422286119 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.107543722229227 0.339991694852011 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.94245 | 38.2918 | 0 | 2491480.80884786 | -9511955.31778503 | 10619937.2978881 | 10.6199 | 11 | 24.0842
gen_3454_2 | 24713010.7383127 | 11000 | 50 | 1300 | 4 | 0 | 0.139443754817708 | 0.2758433507203775 | 1.10337340288151 | 0.553268195697572 | 0.258397505886387 | 0.186795227232389 | 0.186795227232389 | 10 | 5.97985164252343 | 0.152448674468719 | 0.0579157009681687 | 0.01 | 0 | 1 | 1 | 3.04276347701065 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.110582654210106 0.328403992902662 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9398 | 41.6558 | 18586411.6902135 | 1855504.098476 | -9455394.026055001 | 10633135.8696334 | 10.6331 | 11 | 24.713
gen_3455_3 | 23697435.0718665 | 11000 | 50 | 1300 | 4 | 0 | 0.135863187787472 | 0.2701580933232675 | 1.08063237329307 | 0.5450917308186179 | 0.259573580621509 | 0.184251038159709 | 0.184251038159709 | 10 | 5.91066214907914 | 0.152371044559637 | 0.0585304443674162 | 0.01 | 0 | 1 | 1 | 3.05121519623231 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.110161959833577 0.337843681309663 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.94267 | 41.6379 | 18792232.4971296 | 2315867.51971524 | -9592254.3202294 | 10825806.1378729 | 10.8258 | 11 | 23.6974
gen_3456_4 | 24581863.8734054 | 11000 | 50 | 1300 | 4 | 0 | 0.139666955534485 | 0.2729835293692425 | 1.09193411747697 | 0.5663466325169429 | 0.255758276960114 | 0.186317456903402 | 0.186317456903402 | 10 | 5.96565050280886 | 0.153289203950041 | 0.0585229253903031 | 0.01 | 0 | 1 | 1 | 3.06111575495359 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.10631581778951 0.329448775223282 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.93537 | 38.3705 | -502148.6751968039 | 570948.0673572051 | -9784020.396228882 | 10797096.3336993 | 10.7971 | 11 | 24.5819
gen_3457_5 | 8765142.553886401 | 6600.0 | 50 | 1300 | 4 | 0 | 0.135675959777785 | 0.268288888149715 | 1.07315555259886 | 0.549201534618158 | 0.25611996492371 | 0.188679827526212 | 0.188679827526212 | 10 | 5.90421553250868 | 0.158422106663394 | 0.0570922884592786 | 0.01 | 0 | 1 | 1 | 3.01350850557629 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.109583096316978 0.342370632514881 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01518 | 37.6743 | 95861.40023078769 | 777090.3171950489 | -3280304.42381278 | 4266772.48822525 | 4.2668 | 6.6 | 8.7651
gen_3462_1 | 195968994.493899 | 11000 | 50 | 1300 | 4 | 0 | 0.20213662038655 | 0.659242306136585 | 2.63696922454634 | 2.60532179370057 | 0.356630612569861 | 0.65147003647997 | 0.240594708883669 | 0.240594708883669 | 9.988602927371399 | 2.56252056546509 | 0.0459457762856036 | 0.153269049965311 | 0 | 1 | 1 | 6.02134603490704 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.130303922620299 0.396977485469589 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00347 | 49.4807 | 149137694.83177 | -11938774.3127884 | -65562756.31114841 | 83368404.08742429 | 83.3684 | 11 | 195.969
gen_3463_1 | 105795435.098372 | 10500.0 | 50 | 1300 | 4 | 0 | 0.135855539930798 | 0.5600968019324924 | 2.24038720772997 | 2.07808341637021 | 0.273113670934318 | 0.472653432922438 | 0.175374579555728 | 0.175374579555728 | 8.665996484808529 | 2.57883605716052 | 0.0503824694449548 | 0.150552357514389 | 0 | 1 | 1 | 4.51023245711694 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.120702845322853 0.525762239581905 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.92011 | 52.4676 | 78570127.64308451 | 7658191.48109229 | -37966390.5780572 | 49840034.8263651 | 49.84 | 10.5 | 105.7954
gen_3464_1 | 189740778.37402 | 10500.0 | 50 | 1300 | 4 | 0 | 0.234970570188016 | 0.6467035999381625 | 2.58681439975265 | 2.1410347990822 | 0.292815330756642 | 1.5162614585096 | 0.241665739247855 | 0.241665739247855 | 10.4732344514504 | 3.45203370006289 | 0.045548999259132 | 0.422605552948779 | 0 | 1 | 1 | 6.28164900460839 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.125669128373265 0.461689355796017 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00491 | 42.3329 | 122659723.240664 | -4114679.43222821 | -43562894.29795 | 75681370.99780139 | 75.6814 | 10.5 | 189.7408
gen_3466_1 | 34700242.9670887 | 33000 | 50 | 1300 | 4 | 0 | 0.100544154949021 | 0.5354111614278525 | 2.14164464571141 | 1.07322426255606 | 0.264532680691266 | 1.0535195200108 | 0.174331337062223 | 0.174331337062223 | 3.85515368472785 | 0.800921465251595 | 0.486007277850062 | 0.0811903934385628 | 0 | 1 | 1 | 0.889749546607677 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.254026163375238 0.748099787806929 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99805 | 43.274 | 28531546.5193212 | -5976465.87355519 | -12621291.1846116 | 12835821.2239109 | 12.8358 | 33 | 34.7002
gen_3525_2 | 223215363.41426 | 15750.00 | 50 | 1300 | 4 | 0 | 0.170384856407298 | 0.6404796050221775 | 2.56191842008871 | 2.46432616055664 | 0.262067336944165 | 0.415023805266246 | 0.190478047210025 | 0.190478047210025 | 10.5113917976534 | 0.948073863982223 | 0.0210824453208363 | 0.0322791219606996 | 0 | 1 | 1 | 7.11769991533365 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.119813104767259 0.477150379756652 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98699 | 51.7711 | 151481625.780188 | -3180323.97998087 | -52160656.4629599 | 88333471.87093641 | 88.3335 | 15.75 | 223.2154
gen_3526_3 | 230990713.269683 | 15750.00 | 50 | 1300 | 4 | 0 | 0.170576797550311 | 0.6591896275808675 | 2.63675851032347 | 2.39513134009298 | 0.260411747399485 | 0.414466611137614 | 0.196436051865341 | 0.196436051865341 | 10.2293869178845 | 0.965527558209607 | 0.0218661442307755 | 0.0330936538539827 | 0 | 1 | 1 | 7.18924208271783 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.121039913816038 0.482770825374545 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98381 | 52.3544 | 162320706.638927 | -6577040.77966753 | -49809372.3358709 | 93677103.93004189 | 93.6771 | 15.75 | 230.9907
gen_3527_1 | 225237187.795574 | 15750.00 | 50 | 1300 | 4 | 0 | 0.170470155445393 | 0.6629519883183524 | 2.65180795327341 | 2.470071141202 | 0.256666094687534 | 0.403817578935996 | 0.193139204173116 | 0.193139204173116 | 10.5212591934707 | 0.9691151317872569 | 0.0216991204970051 | 0.0326575705833733 | 0 | 1 | 1 | 7.30375274606049 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.123148533204449 0.477072804204561 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99662 | 51.2158 | 134162182.604531 | 10374154.2792809 | -54101183.2628633 | 88027697.02047099 | 88.0277 | 15.75 | 225.2372
gen_3585_1 | 416378375.744331 | 20000 | 50 | 1300 | 4 | 0 | 0.286182851218502 | 0.564136743018375 | 2.2565469720735 | 1.6770294983146 | 0.321704444057308 | 0.402020928110299 | 0.306198669456621 | 0.306198669456621 | 5.03132362128235 | 2.01377022638917 | 0.0281767686988693 | 0.23915942830476 | 0 | 1 | 1 | 2.74490874500852 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09769925569263289 0.296640700748144 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.0065 | 71.51309999999999 | 333830986.389622 | 18201650.0208466 | -84600220.37755139 | 187426987.361648 | 187.427 | 20 | 416.3784
gen_3586_2 | 426822030.8 | 20000 | 50 | 1300 | 4 | 0 | 0.279518983141054 | 0.568703848772885 | 2.27481539509154 | 1.74322218769863 | 0.31709007694535 | 0.403299651146959 | 0.296057862785854 | 0.296057862785854 | 5.03224208392203 | 2.04006330519915 | 0.027402938270336 | 0.238587287424132 | 0 | 1 | 1 | 2.73753789174743 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0954707451985683 0.295126953427708 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00423 | 71.7016 | 331572555.586178 | 14097260.140581 | -85068206.0364242 | 187669186.300988 | 187.6692 | 20 | 426.822
gen_3587_3 | 423626371.387602 | 20000 | 50 | 1300 | 4 | 0 | 0.281319335393957 | 0.570048846006975 | 2.2801953840279 | 1.74486660734506 | 0.320744155808352 | 0.404966220451379 | 0.303982554954616 | 0.303982554954616 | 5.168982744799 | 2.04926389493048 | 0.0273757392545929 | 0.239704781253589 | 0 | 1 | 1 | 2.71798191038147 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0948291099937633 0.292491000939277 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99478 | 66.7197 | 136302122.333584 | -16738082.6868276 | -123132548.622373 | 146622900.48844 | 146.6229 | 20 | 423.6264
gen_3588_4 | 515843401 | 20000 | 50 | 1300 | 4 | 0 | 0.278137262566527 | 0.5720967587517225 | 2.28838703500689 | 1.75201769268094 | 0.319455117593519 | 0.409774367539654 | 0.300327728850185 | 0.300327728850185 | 5.13414660817944 | 2.02966636954807 | 0.0273117118729278 | 0.234778617666801 | 0 | 1 | 1 | 2.74790081625897 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.09550755948787561 0.297212320385221 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00248 | 71.51860000000001 | 349539415.874761 | 9086868.038214741 | -85198301.8893601 | 184270663.669502 | 184.2707 | 20 | 515.8434
gen_3655_1 | 579866190.144909 | 19000 | 50 | 1300 | 4 | 0 | 0.193236772105796 | 0.536179720030165 | 2.14471888012066 | 1.81843981607258 | 0.306154155093245 | 1.05026188927819 | 0.220684786459897 | 0.220684786459897 | 7.23080071737408 | 1.59401434882428 | 0.0209646982420236 | 0.251462698238902 | 0 | 1 | 1 | 2.18888416496571 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.07986746050357819 0.244492200583038 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00366 | 44.4172 | 367584851.894179 | 41030505.5378158 | -178142572.029121 | 223737480.013492 | 223.7375 | 19 | 579.8662
gen_3656_2 | 566034920.721082 | 19000 | 50 | 1300 | 4 | 0 | 0.196368822226766 | 0.5421152264690025 | 2.16846090587601 | 1.80948558315402 | 0.304449887098744 | 1.08558250523871 | 0.227739578544162 | 0.227739578544162 | 7.16370960273896 | 1.55405060914112 | 0.0209569999435917 | 0.25156340522808 | 0 | 1 | 1 | 2.2019494577134 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0786993845665455 0.243997724476 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.0051 | 44.4101 | 364291288.39322 | 48745432.587144 | -182997046.562657 | 220587290.059822 | 220.5873 | 19 | 566.0349
gen_4003_1 | 36283948.1079485 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.15678730553831 | 0.2934641098859725 | 1.17385643954389 | 0.5844911312768239 | 0.283242659330368 | 0.187902769177337 | 0.187902769177337 | 10 | 9.17843924118206 | 0.156655647353036 | 0.054201855822932 | 0.01 | 0 | 1 | 1 | 3.97934499998158 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.130051803027513 0.593210874324664 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.99352 | 70.0615 | 27496747.6991704 | -197728.151173517 | -223021.069807373 | 219363.540039561 | 0.21936 | 0.69 | 36.2839
gen_4007_1 | 121983711.870527 | 1000 | 50 | 1300 | 4 | 0 | 0.155252380674938 | 0.289299014913675 | 1.1571960596547 | 0.591163104061037 | 0.289727672589943 | 0.187455511361128 | 0.187455511361128 | 10 | 9.36529112092685 | 0.154809081167914 | 0.0526004907934926 | 0.01 | 0 | 1 | 1 | 4.09748774960963 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.135579899418633 0.587289435290266 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.99873 | 58.7091 | 80896908.53776619 | 4976529.913062599 | -20219328.893 | 10099234.705 | 10.0992 | 1 | 121.9837
gen_4008_1 | 21604431.1194727 | 1000 | 50 | 1300 | 4 | 0 | 0.151160391656449 | 0.295109193776735 | 1.18043677510694 | 0.599822156392038 | 0.285328818768263 | 0.192075576484087 | 0.192075576484087 | 10 | 9.292492064600809 | 0.153276560122613 | 0.0529066271455958 | 0.01 | 0 | 1 | 1 | 3.93874299145839 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.132764551453758 0.608734394371044 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9941 | 56.5658 | 17264698.250152 | 655523.6094314611 | -698904.260466341 | 718534.689576132 | 0.71853 | 1 | 21.6044
gen_4027_1 | 36261937.3 | 11500.0 | 50 | 1300 | 4 | 0 | 0.206326000192203 | 0.8276675732114825 | 3.31067029284593 | 2.90521842113486 | 0.364900018619536 | 0.524982509855181 | 0.291972666970454 | 0.291972666970454 | 6.92759781420697 | 2.21503148312215 | 0.0410523054329678 | 0.0402912167338654 | 0 | 1 | 1 | 0.638568286315212 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.146712868638802 0.413700690531591 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98064 | 43.6271 | 0 | 3575255.04164393 | -8761768.545582891 | 23659881.5813195 | 23.6599 | 11.5 | 36.2619
gen_4028_1 | 37226840 | 11500.0 | 50 | 1300 | 4 | 0 | 0.205050811241381 | 0.7959422592825725 | 3.18376903713029 | 2.9652172489115 | 0.360967097370303 | 0.520752102683764 | 0.292826108609908 | 0.292826108609908 | 6.74260334243998 | 2.21459018998314 | 0.041636662135832 | 0.0414714867752045 | 0 | 1 | 1 | 0.650970138574322 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.14277624659054 0.404808979857806 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98165 | 43.6271 | 0 | 3753285.38779309 | -8543905.67094088 | 23928625.7288768 | 23.9286 | 11.5 | 37.2268
gen_4029_1 | 36524171.1 | 11500.0 | 50 | 1300 | 4 | 0 | 0.208778605675325 | 0.795947279379935 | 3.18378911751974 | 2.94997158876411 | 0.367285415659053 | 0.52246138874907 | 0.287282751769409 | 0.287282751769409 | 6.8490337250568 | 2.22632003779057 | 0.0408653176035732 | 0.0403539084820077 | 0 | 1 | 1 | 0.635884067243268 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.145386544555426 0.40066567151933 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9734699999999999 | 43.6271 | 0 | 258818.292321265 | -8648045.37352174 | 24515034.4303111 | 24.515 | 11.5 | 36.5242
gen_4030_1 | 37020949.1 | 11500.0 | 50 | 1300 | 4 | 0 | 0.207042969288304 | 0.8114360498571775 | 3.24574419942871 | 2.89404749008431 | 0.37042945535311 | 0.518581234419253 | 0.297246730734827 | 0.297246730734827 | 6.90915627587121 | 2.21485167982522 | 0.0410489713214338 | 0.0408038992714137 | 0 | 1 | 1 | 0.630729210312665 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.145483384316321 0.411864801630704 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.98277 | 43.6271 | 0 | 4239968.87961002 | -8637836.731038989 | 24036779.6063656 | 24.0368 | 11.5 | 37.0209
gen_4033_1 | 37283358.7994021 | 11500.0 | 50 | 1300 | 4 | 0 | 0.207235419228673 | 0.8084679086366675 | 3.23387163454667 | 2.93847436736571 | 0.355066767665744 | 0.514116341434419 | 0.295284240628593 | 0.295284240628593 | 6.68756683983374 | 2.22052502406761 | 0.0410490254191682 | 0.0419163630865514 | 0 | 1 | 1 | 0.639498501921888 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.144497200919781 0.399766729901964 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.97606 | 44.1752 | 0 | 1932270.16302422 | -8604334.55165476 | 23784596.585494 | 23.7846 | 11.5 | 37.2834
gen_4034_1 | 37528516.240641 | 11500.0 | 50 | 1300 | 4 | 0 | 0.203006632858887 | 0.8162936026647225 | 3.26517441065889 | 3.03361017050082 | 0.35693370004138 | 0.518068545253482 | 0.293150664801244 | 0.293150664801244 | 6.62671143864747 | 2.24587251405232 | 0.0409542281460017 | 0.0406969609949738 | 0 | 1 | 1 | 0.627455456197425 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.141204250569455 0.413058329032175 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9660300000000001 | 44.1752 | 0 | 1952267.824 | -8448062.14440614 | 23818713.4763575 | 23.8187 | 11.5 | 37.5285
gen_4035_1 | 36390120.1120326 | 11500.0 | 50 | 1300 | 4 | 0 | 0.205308668892831 | 0.8088157449744175 | 3.23526297989767 | 3.02947285106359 | 0.368124124032655 | 0.505550011212472 | 0.296604644083651 | 0.296604644083651 | 6.7742420677375 | 2.20991613238119 | 0.0418790184557438 | 0.0416608289591968 | 0 | 1 | 1 | 0.635680062490469 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.14528441200126 0.403249115825677 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.9779 | 44.1752 | 0 | 3338155.2571319 | -8464857.105910782 | 23682589.4860667 | 23.6826 | 11.5 | 36.3901
gen_4036_1 | 36140879.8766029 | 11500.0 | 50 | 1300 | 4 | 0 | 0.203116274396889 | 0.829442892221735 | 3.31777156888694 | 2.99994834688795 | 0.362317013765639 | 0.504290030198172 | 0.289618320174166 | 0.289618320174166 | 6.72339465667494 | 2.28254319244996 | 0.0407950328448787 | 0.0415979244560003 | 0 | 1 | 1 | 0.631181208406319 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.144726410932373 0.403998799578985 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.97693 | 44.1752 | 0 | 2952519.72554466 | -8506062.23549694 | 24083396.9847299 | 24.0834 | 11.5 | 36.1409
gen_4051_1 | 89957086.3413974 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.151992672766792 | 0.2951559283213575 | 1.18062371328543 | 0.589005427686963 | 0.288138393905014 | 0.19326474353706 | 0.19326474353706 | 10 | 9.43565296875313 | 0.150356083600782 | 0.0530004094565287 | 0.01 | 0 | 1 | 1 | 4.07913892430207 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.130269146872917 0.596963295393623 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.09411 | 76.7192 | 70775031.9602899 | 6074.88999310881 | -15006561.913253 | 5006546.884034 | 5.0065 | 0.69 | 89.9571
gen_4052_11 | 198828031.233628 | 15750.00 | 50 | 1300 | 4 | 0 | 0.150394752274733 | 0.5965474841522524 | 2.38618993660901 | 2.16149507364677 | 0.223018523057457 | 0.351871006223373 | 0.177066295860335 | 0.177066295860335 | 5.96803053396195 | 1.01625046047312 | 0.0229278964031488 | 0.0346846397274174 | 0 | 1 | 1 | 9.209414504291489 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.122499680684879 0.47059609410353 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99553 | 51.276 | 127264972.509581 | 7903512.92538997 | -71342037.42085959 | 88723222.660739 | 88.7232 | 15.75 | 198.828
gen_4053_12 | 194910538.269533 | 15750.00 | 50 | 1300 | 4 | 0 | 0.157130740061402 | 0.6036265549005475 | 2.41450621960219 | 2.14257960294001 | 0.227537203013897 | 0.358970360463718 | 0.178184728439432 | 0.178184728439432 | 6.06553120166436 | 1.01559444761742 | 0.0228931397322565 | 0.0340843847026583 | 0 | 1 | 1 | 9.063417786185161 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.125413441236131 0.484584687893512 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99759 | 51.2282 | 135210093.454782 | 11477315.2025951 | -71398716.37816541 | 85954802.87179819 | 85.9548 | 15.75 | 194.9105
gen_4054_18 | 203925937.385531 | 15750.00 | 50 | 1300 | 4 | 0 | 0.155965819212142 | 0.58947345005552 | 2.35789380022208 | 2.14296053675888 | 0.23191395131615 | 0.367635045382194 | 0.176058569985325 | 0.176058569985325 | 6.03764258647151 | 1.03706964065926 | 0.0229919012343977 | 0.034806307345489 | 0 | 1 | 1 | 8.14038782794727 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.13204855687893 0.430876162364613 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99607 | 52.171 | 137629578.773985 | 9789118.596352641 | -70956120.51626669 | 88457155.35767379 | 88.4572 | 15.75 | 203.9259
gen_4058_1 | 162354895.274621 | 13800.0 | 50 | 1300 | 4 | 0 | 0.206327513656579 | 0.54238441960048 | 2.16953767840192 | 1.59470540627162 | 0.33853507436784 | 0.419636959563941 | 0.307269243356395 | 0.307269243356395 | 5.63698048211052 | 0.726625784244388 | 0.0506218219106086 | 0.102953386534937 | 0 | 1 | 1 | 5.4514807471307 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.171841255335836 0.517091084865388 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00101 | 49.2863 | 38494684.4491548 | 16763116.6103504 | 0 | 61223826.4574204 | 61.2238 | 13.8 | 162.3549
gen_4059_2 | 159278157.002991 | 13800.0 | 50 | 1300 | 4 | 0 | 0.205749020562507 | 0.5221725440230225 | 2.08869017609209 | 1.62818475317373 | 0.335911991840135 | 0.416023704865947 | 0.301625064722481 | 0.301625064722481 | 5.81185808123206 | 0.724394014978316 | 0.0516085953789297 | 0.104392981084529 | 0 | 1 | 1 | 5.32272242852952 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.177794018537272 0.512371368694585 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99526 | 49.257 | 37308413.7147125 | 11740120.5939442 | 0 | 61116945.1517053 | 61.1169 | 13.8 | 159.2782
gen_4061_4 | 159933895.852882 | 13800.0 | 50 | 1300 | 4 | 0 | 0.201001975690015 | 0.5310093617159874 | 2.12403744686395 | 1.66299619626347 | 0.336042857806105 | 0.400268676634878 | 0.300271373260999 | 0.300271373260999 | 5.6157100670028 | 0.719611669196747 | 0.0519176516891457 | 0.100536718044896 | 0 | 1 | 1 | 5.38528578400845 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.171242699662223 0.5128988242358899 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00174 | 49.0832 | 38770804.742195 | 18323136.900162 | 0 | 61441359.1394201 | 61.4414 | 13.8 | 159.9339
gen_4062_1 | 266940658.88878 | 16000 | 50 | 1300 | 4 | 0 | 0.203523496957496 | 0.48675963286485 | 1.9470385314594 | 1.98192206219537 | 0.282545331689436 | 0.570550813626498 | 0.225983217998967 | 0.225983217998967 | 6.40017122149468 | 1.20413972176285 | 0.0405958254551515 | 0.0331877614304423 | 0 | 1 | 1 | 3.71073684319854 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.133453439018223 0.572741040422116 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00541 | 49.2231 | 55875072.0689865 | 12202752.1266136 | -43588679.1613652 | 102605515.642208 | 102.6055 | 16 | 266.9407
gen_4064_3 | 272704311.920097 | 16000 | 50 | 1300 | 4 | 0 | 0.205531044285744 | 0.50477326384012 | 2.01909305536048 | 1.99154805296706 | 0.286583961114474 | 0.581868880489841 | 0.219337989206985 | 0.219337989206985 | 6.45610193923116 | 1.23758522977959 | 0.0407054398311302 | 0.0325030825398862 | 0 | 1 | 1 | 3.76831985305063 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.132293339465745 0.5578299672517461 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01184 | 49.4661 | 61313445.7642919 | 19010021.6837332 | -44697540.6577112 | 102179665.919766 | 102.1797 | 16 | 272.7043
gen_4065_4 | 262876889.418112 | 16000 | 50 | 1300 | 4 | 0 | 0.208191523430869 | 0.50358357649867 | 2.01433430599468 | 1.98178839047998 | 0.281459558275994 | 0.560561018139124 | 0.223078246046975 | 0.223078246046975 | 6.6274527862668 | 1.22703910976136 | 0.0418088025366887 | 0.0325258976228535 | 0 | 1 | 1 | 3.66887286957353 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.132835075129289 0.567994472252904 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.00877 | 49.4007 | 58176223.5661949 | 15919317.246771 | -43971128.0946154 | 105959633.671166 | 105.9596 | 16 | 262.8769
gen_4066_1 | 175505024.693906 | 15750.00 | 50 | 1300 | 4 | 0 | 0.155368680819869 | 0.60153904773295 | 2.4061561909318 | 1.7430849492806 | 0.224632904800586 | 0.885276040819683 | 0.181146601661108 | 0.181146601661108 | 13.1314481748268 | 3.29759017562494 | 0.0204176598712802 | 0.0916507558718789 | 0 | 1 | 1 | 6.96312351168133 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.172373836642802 0.457313768823195 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01738 | 50.8848 | 78796676.5485445 | 5715587.193107 | -37492361.4150464 | 63159811.665549 | 63.1598 | 15.75 | 175.505
gen_4067_2 | 88515861.5344204 | 11500.0 | 50 | 1300 | 4 | 0 | 0.166284906353592 | 0.464406105964735 | 1.85762442385894 | 1.55376504692249 | 0.25109557152912 | 0.6944936321191491 | 0.217818839299027 | 0.217818839299027 | 11.023837137199 | 1.50445765501354 | 0.0203490700470284 | 0.124218902628869 | 0 | 1 | 1 | 4.62459111272357 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.112281255816171 0.579237865740879 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.01721 | 51.6451 | 49608791.4977608 | 5563277.93701654 | -17900387.1763423 | 35972756.9751696 | 35.9728 | 11.5 | 88.5159
gen_4072_1 | 50093021.3746056 | 11000 | 50 | 1300 | 4 | 0 | 0.158843087055115 | 0.4955897862495625 | 1.98235914499825 | 1.0053735620528 | 0.283952252129093 | 0.368525704099913 | 0.234599338155985 | 0.234599338155985 | 5.24826739054872 | 2.84290729199213 | 0.0405561378989369 | 0.0327926296308637 | 0 | 1 | 1 | 1.98785841308534 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.217126812126255 0.854401902809273 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.0036 | 48.563 | 38611398.4149723 | -1447468.11458711 | -16818697.6697296 | 20589500.5164901 | 20.5895 | 11 | 50.093
gen_4078_11 | 34967409.21 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.150826305462979 | 0.2874148914692925 | 1.14965956587717 | 0.600045177151449 | 0.281397389925085 | 0.188476831981447 | 0.188476831981447 | 10 | 9.29321550414898 | 0.156875069002854 | 0.0534858602050692 | 0.01 | 0 | 1 | 1 | 3.91619372858945 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.132571890313644 0.586623261474539 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.0024 | 59.8542 | 22818891.8386586 | -7020941.58437103 | -7664210.99454165 | 7442999.83186647 | 7.443 | 0.69 | 34.9674
gen_4079_12 | 100765322.4 | 689.9999999999999000 | 50 | 1300 | 4 | 0 | 0.152027188693173 | 0.2894250309343325 | 1.15770012373733 | 0.593313001164701 | 0.282097413945943 | 0.192326170376968 | 0.192326170376968 | 10 | 9.000116564193741 | 0.152052130030934 | 0.0530122577400878 | 0.01 | 0 | 1 | 1 | 3.94851786133042 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.132173920214409 0.584840002771933 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00267 | 60.2181 | 17313522.3124386 | -4972803.44702303 | -5252761.26880199 | 5212099.18666631 | 5.2121 | 0.69 | 100.7653
gen_4081_2 | 77611180.44 | 1000 | 50 | 1300 | 4 | 0 | 0.156753281643614 | 0.2834964207565075 | 1.13398568302603 | 0.600816943613812 | 0.286708662318997 | 0.192364343761466 | 0.192364343761466 | 10 | 9.233899371488951 | 0.155092288947199 | 0.0524527228628285 | 0.01 | 0 | 1 | 1 | 3.9770387449814 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.133919472242007 0.592968022181187 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01253 | 70.6331 | 63226850.6484948 | 6521236.869879629 | -21980508.199 | 11909516.936 | 11.9095 | 1 | 77.6112
gen_4082_3 | 109932953.7 | 1000 | 50 | 1300 | 4 | 0 | 0.153208841144806 | 0.29221099415829 | 1.16884397663316 | 0.5979652850278649 | 0.28833330417797 | 0.191972146908753 | 0.191972146908753 | 10 | 9.395676630106751 | 0.152527046041796 | 0.0532631505943835 | 0.01 | 0 | 1 | 1 | 3.94146927141561 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.130500552000711 0.590768476321362 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.96231 | 70.6949 | 93216660.2577516 | -26255097.8837705 | -31140036.9320298 | 31408483.860828 | 31.4085 | 1 | 109.933
gen_4083_4 | 50331527.63 | 1000 | 50 | 1300 | 4 | 0 | 0.153164466423914 | 0.292150312308165 | 1.16860124923266 | 0.597276761271991 | 0.281930342026055 | 0.18944713531679 | 0.18944713531679 | 10 | 9.072410927480091 | 0.154496698463336 | 0.054348768913094 | 0.01 | 0 | 1 | 1 | 4.03938563412428 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.13162055727141 0.580039693395607 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9821299999999999 | 70.49160000000001 | 38318988.2633566 | -2394380.55101959 | -6106830.9832802 | 6175535.15918693 | 6.1755 | 1 | 50.3315
gen_5004_1 | 147696965.934895 | 13800.0 | 50 | 1300 | 4 | 0 | 0.18852995700622 | 0.2488115041930125 | 0.99524601677205 | 0.821763478043268 | 0.344339294709731 | 0.261126842256635 | 0.261126842256635 | 10 | 8.74702504477464 | 0.132720764507353 | 0.0711697793488857 | 0.01 | 0 | 1 | 1 | 3.66786438781908 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.126354949656867 0.668281596952546 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98803 | -11.167 | 100949965.172718 | 15858097.1790647 | -88039735.0739222 | 103178625.964909 | 103.1786 | 13.8 | 147.697
gen_5005_2 | 147170128.862932 | 13800.0 | 50 | 1300 | 4 | 0 | 0.18503765401477 | 0.2942086525436025 | 1.17683461017441 | 0.716933679748327 | 0.38534526446485 | 0.340287405041512 | 0.340287405041512 | 10 | 10.4756066911179 | 0.0499426819268614 | 0.082799718471244 | 0.01 | 0 | 1 | 1 | 3.83138867123635 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.16493288499862 0.360802925336175 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98282 | -11.1988 | 101988012.94916 | 11223793.7533833 | -103961025.919649 | 112744375.113212 | 112.7444 | 13.8 | 147.1701
gen_5006_1 | 99826822.90775701 | 13800.0 | 50 | 1300 | 4 | 0 | 0.101724166010972 | 0.252783072046935 | 1.01113228818774 | 0.553383511886001 | 0.174827369039645 | 0.145292613220634 | 0.145292613220634 | 10 | 7.59521613064688 | 0.174535932511487 | 0.07492338583823289 | 0.01 | 0 | 1 | 1 | 3.80142738206545 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.184031333498284 0.542391815814152 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9882 | -9.721500000000001 | 73446184.7861416 | 11707272.6332725 | -37692884.8471694 | 53654592.7810948 | 53.6546 | 13.8 | 99.8268
gen_5008_1 | 59560990.06 | 11000 | 50 | 1300 | 4 | 0 | 0.142380864560977 | 0.31643721961882 | 1.26574887847528 | 0.839073885753751 | 0.388478278086521 | 0.260877983275335 | 0.260877983275335 | 10 | 8.23614376574289 | 0.563970345699927 | 0.220169016325381 | 0.01 | 0 | 1 | 1 | 3.20729808327276 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.128608798471396 0.457621719811577 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.05511 | -16.8894 | 47216573.469236 | 1213641.35779217 | -12695080.0597709 | 11685417.1768175 | 11.6854 | 11 | 59.561
gen_5010_1 | 123244468.957768 | 13800.0 | 50 | 1300 | 4 | 0 | 0.153043946614489 | 0.3234723457974025 | 1.29388938318961 | 0.7116745720347391 | 0.315454478991916 | 0.248701347889379 | 0.248701347889379 | 10 | 9.55923343802802 | 0.221254664713051 | 0.08602358342721129 | 0.01 | 0 | 1 | 1 | 3.17207759841112 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.155571648985008 0.502723538072314 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98159 | -22.6446 | -1437843.02386409 | -6768.52515642531 | -70406023.237661 | 83832183.03075989 | 83.8322 | 13.8 | 123.2445
gen_5012_1 | 37868305.058335 | 11000 | 50 | 1300 | 4 | 0 | 0.154325268304674 | 0.31332075052592 | 1.25328300210368 | 0.6501649588178841 | 0.282818324382417 | 0.209052208983339 | 0.209052208983339 | 10 | 6.1387404654175 | 0.185631442188285 | 0.0487754687140929 | 0.01 | 0 | 1 | 1 | 3.01769822124741 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.226847723557148 0.756103740836726 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9472699999999999 | -24.5186 | 2054325.35428554 | -3695504.50593 | -11850309.1197205 | 14740269.701425 | 14.7403 | 11 | 37.8683
gen_5016_6 | 72603132.7684186 | 11500.0 | 50 | 1300 | 4 | 0 | 0.148048650905234 | 0.6207415717325649 | 2.48296628693026 | 1.9367207089148 | 0.202967797270976 | 0.261927351441234 | 0.192224249258754 | 0.192224249258754 | 9.081384618370789 | 0.820173190496862 | 0.0501156165834982 | 0.0513946956919972 | 0 | 1 | 1 | 1.25006516969763 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.0781780890945811 0.389785741567006 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 0.99307 | -21.6029 | 49579877.53745349 | -7535040.49162455 | -26664161.2693365 | 46168054.2550115 | 46.1681 | 11.5 | 72.6031
gen_5017_1 | 192647608.940816 | 14500.0 | 50 | 1300 | 4 | 0 | 0.107299279139843 | 0.5157990052463125 | 2.06319602098525 | 1.74826330939308 | 0.193334957496822 | 0.625304266330786 | 0.157140769721009 | 0.157140769721009 | 8.84829626792343 | 1.2809844690403 | 0.0700780015490018 | 0.0902931747429538 | 0 | 1 | 1 | 6.32548919849815 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.198745998335816 0.771605615922101 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.05574 | -20.9527 | 137396424.963428 | 23132332.6218313 | -38910738.3759441 | 119704536.603408 | 119.7045 | 14.5 | 192.6476
gen_5018_2 | 96002555.5250328 | 13200.0 | 50 | 1300 | 4 | 0 | 0.146977232673694 | 0.5749339060363124 | 2.29973562414525 | 1.91000741438824 | 0.255677304739668 | 0.627477423870005 | 0.185621718681883 | 0.185621718681883 | 5.73168120799819 | 0.507553317747079 | 0.0205177206187509 | 0.0209077860121615 | 0 | 1 | 1 | 7.12228956878535 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 0 | 3 | 2 | [0.8 0.12254166426044 0.553614712604321 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 2 | G | 1.05271 | -21.2257 | 64711473.4428376 | 8644864.607815819 | -18359682.3917715 | 60562258.0148267 | 60.5623 | 13.2 | 96.0026
gen_5019_1 | 16427802.1572973 | 11000 | 50 | 1300 | 4 | 0 | 0.184275091849733 | 0.329393194384175 | 1.3175727775367 | 0.86042637053947 | 0.290093605467817 | 0.226428245000541 | 0.226428245000541 | 10 | 5.08864011024823 | 0.0506473413563799 | 0.0403257830180228 | 0.01 | 0 | 1 | 1 | 3.5755401427187 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.148136353833452 0.373060623571973 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.05495 | -7.1724 | 9824507.83043848 | 50819.8441695888 | -5930855.29242624 | 10640462.8411658 | 10.6405 | 11 | 16.4278
gen_5020_1 | 40330566.31 | 11000 | 50 | 1300 | 4 | 0 | 0.134963406756986 | 0.3810283620997225 | 1.52411344839889 | 1.01153627024861 | 0.331986889290344 | 0.311260443435982 | 0.311260443435982 | 10 | 8.1213656418398 | 0.052081095239846 | 0.0510424262552988 | 0.01 | 0 | 1 | 1 | 2.83653903900413 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0366475281999447 0.260852762719151 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.04821 | -6.7953 | 34931952.5974112 | 9933.722652494909 | -12126771.8605092 | 19686562.1649055 | 19.6866 | 11 | 40.3306
gen_5021_4 | 40079519.2 | 11000 | 50 | 1300 | 4 | 0 | 0.113523972480558 | 0.3277596861496575 | 1.31103874459863 | 0.844808232254558 | 0.221801029459969 | 0.202375394717208 | 0.202375394717208 | 10 | 7.74166894327733 | 0.0520080470480025 | 0.0520592333364766 | 0.01 | 0 | 1 | 1 | 2.793804211932 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0756900096446276 0.255148485631705 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.05035 | -7.1268 | 32308907.6933498 | 941951.6572624909 | -12454219.313194 | 12143054.1370763 | 12.1431 | 11 | 40.0795
gen_5022_1 | 33646398.6921869 | 11000 | 50 | 1300 | 4 | 0 | 0.198508361308137 | 0.2781714209972425 | 1.11268568398897 | 0.689297532958444 | 0.323259469884913 | 0.236117589125643 | 0.236117589125643 | 10 | 8.794950967328621 | 0.296337645051768 | 0.0571208542329259 | 0.01 | 0 | 1 | 1 | 3.10728719173116 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0483750213727355 0.220065048394725 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00571 | -6.0398 | 24963966.1360357 | 239045.050738007 | -4144594.91161164 | 12872827.8792766 | 12.8728 | 11 | 33.6464
gen_5023_2 | 33327303.1253414 | 11000 | 50 | 1300 | 4 | 0 | 0.191337353344774 | 0.2951254563045225 | 1.18050182521809 | 0.678727157317801 | 0.292724154486554 | 0.230609839008423 | 0.230609839008423 | 10 | 8.505664929847701 | 0.296561451896094 | 0.0552932796410751 | 0.01 | 0 | 1 | 1 | 3.05276727499324 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.061208732411731 0.234609147235518 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.0064 | -6.0454 | 24074777.1746134 | 463680.075544119 | -4153276.83904674 | 12896859.0873806 | 12.8969 | 11 | 33.3273
gen_5026_5 | 34233340.8685471 | 11000 | 50 | 1300 | 4 | 0 | 0.197707602338633 | 0.2791817630784925 | 1.11672705231397 | 0.680790583598427 | 0.290301190034254 | 0.236424257267034 | 0.236424257267034 | 10 | 8.890312088392671 | 0.300883624962764 | 0.0573895943954121 | 0.01 | 0 | 1 | 1 | 3.05742282888037 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0458928027772461 0.212981410968583 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00365 | -5.9849 | 24197047.9211855 | -379025.940144062 | -4080205.19196987 | 12951013.3723076 | 12.951 | 11 | 34.2333
gen_5028_1 | 37749957.9498544 | 11000 | 50 | 1300 | 4 | 0 | 0.146029489391949 | 0.3817076594338275 | 1.52683063773531 | 0.931190368100046 | 0.298232134659123 | 0.19172438368178 | 0.19172438368178 | 10 | 5.2067745354725 | 0.0504008927976247 | 0.0510837835329585 | 0.01 | 0 | 1 | 1 | 3.34441089279763 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.103439713951666 0.516975282889325 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.03199 | -9.5951 | 28467912.9616367 | 10404304.9218566 | -6027418.92396854 | 21035087.1851171 | 21.0351 | 11 | 37.75
gen_5030_1 | 53977121.8854003 | 11000 | 50 | 1300 | 4 | 0 | 0.140662283638492 | 0.3485029874456825 | 1.39401194978273 | 0.736305897139013 | 0.343287756925263 | 0.235786713897018 | 0.235786713897018 | 10 | 8.64943542546825 | 0.180747697769199 | 0.0854219186349074 | 0.01 | 0 | 1 | 1 | 3.7682907769829 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.170116121705621 0.562692960999906 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.96138 | -8.062799999999999 | 34362381.8564035 | -10180680.3593985 | -16953172.179811 | 32883658.7648791 | 32.8837 | 11 | 53.9771
gen_5031_1 | 169174009.550363 | 18000 | 50 | 1300 | 4 | 0 | 0.150000232957536 | 0.284239473331895 | 1.13695789332758 | 0.59993613721244 | 0.293749337338842 | 0.189779104838148 | 0.189779104838148 | 10 | 9.041361163789411 | 0.154765920261852 | 0.0537578068670817 | 0.01 | 0 | 1 | 1 | 3.99882500327495 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.131990863871295 0.587945094942581 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.95645 | 0.858 | 105104009.283556 | 3302910.61631516 | -44351617.7679878 | 69934474.452585 | 69.9345 | 18 | 169.174
gen_5032_2 | 175344738.017768 | 18000 | 50 | 1300 | 4 | 0 | 0.151001792532625 | 0.2913045119952575 | 1.16521804798103 | 0.536486257723533 | 0.251639862527372 | 0.193999882639735 | 0.193999882639735 | 10 | 9.287123952137771 | 0.100951359749306 | 0.0103272682637908 | 0.01 | 0 | 1 | 1 | 3.96614725872991 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.16173102060263 0.625932889161631 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.9564 | 0.8236 | 104805398.459447 | 3113070.38174029 | -61813172.6492383 | 76476597.5557431 | 76.4766 | 18 | 175.3447
gen_5033_3 | 168121105.693281 | 18000 | 50 | 1300 | 4 | 0 | 0.153649799219565 | 0.33033053490864 | 1.32132213963456 | 0.730186092278571 | 0.20045689177108 | 0.197674625989841 | 0.197674625989841 | 10 | 9.075324358544311 | 0.0503834899619687 | 0.06294329689163709 | 0.01 | 0 | 1 | 1 | 3.97437572812242 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.21758591457447 0.723073925689096 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | E | 0.9492 | 0 | 85445430.155 | -7136651.074 | -52964055.7177365 | 76612570.2468935 | 76.6126 | 18 | 168.1211
gen_5035_3 | 33765911.3864647 | 11000 | 50 | 1300 | 4 | 0 | 0.152719729563687 | 0.3324290807856025 | 1.32971632314241 | 0.779741670365911 | 0.35684469100507 | 0.270542959116865 | 0.270542959116865 | 10 | 6.81108015392441 | 0.250154000217095 | 0.09003412593388931 | 0.01 | 0 | 1 | 1 | 4.3367640540353 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.155825510529103 0.375505177639891 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.02356 | -18.3995 | 26219989.1117512 | -793026.88851878 | -26058079.3043599 | 31603466.0905134 | 31.6035 | 11 | 33.7659
gen_5036_2 | 36765344.79 | 11000 | 50 | 1300 | 4 | 0 | 0.12207409822382 | 0.328477779476205 | 1.31391111790482 | 0.810418596626027 | 0.276278702782234 | 0.202567852386343 | 0.202567852386343 | 10 | 4.74182861999143 | 0.0521088133030571 | 0.0503703514533118 | 0.01 | 0 | 1 | 1 | 3.6387557173972 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.130004509726446 0.3844666306603 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01721 | -19.4208 | 15942434.7942778 | -4483969.93664932 | -8372556.32321583 | 10196189.0817224 | 10.1962 | 11 | 36.7653
gen_5037_1 | 67989325.93083011 | 16000 | 50 | 1300 | 4 | 0 | 0.120166825281456 | 0.3417731959463575 | 1.36709278378543 | 0.773800725478213 | 0.268367017591372 | 0.154590323728044 | 0.154590323728044 | 10 | 9.36225530854426 | 0.124031776573509 | 0.120159769652411 | 0.01 | 0 | 1 | 1 | 4.44698162184097 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.10233863189118 0.315026509076357 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98842 | -12.1599 | 53384679.52529129 | 2897061.52168536 | -41059067.7038999 | 63485158.8034071 | 63.4852 | 16 | 67.9893
gen_5039_3 | 68369977.0728708 | 16000 | 50 | 1300 | 4 | 0 | 0.12255032122694 | 0.345817406959365 | 1.38326962783746 | 0.759295067272615 | 0.26482190166926 | 0.151491135660326 | 0.151491135660326 | 10 | 9.23990161442198 | 0.124749082532711 | 0.121516685611568 | 0.01 | 0 | 1 | 1 | 4.76331831911812 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.104359039773699 0.325621367128682 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98837 | -13.1707 | 53873371.6477824 | 5237919.69531728 | -39385449.1197271 | 63492386.6791651 | 63.4924 | 16 | 68.37
gen_5040_4 | 66635863.77399039 | 16000 | 50 | 1300 | 4 | 0 | 0.121783336702734 | 0.33797765557235 | 1.3519106222894 | 0.771706657495815 | 0.262631974991411 | 0.15076357232756 | 0.15076357232756 | 10 | 9.168173366552219 | 0.124714353952557 | 0.120458483378403 | 0.01 | 0 | 1 | 1 | 4.7692725137691 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.104809342531953 0.330422795515973 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98685 | -13.2267 | 55893356.14417 | 4376945.288409251 | -39798392.68693469 | 64671274.24897631 | 64.6713 | 16 | 66.6359
gen_5041_5 | 67289418.8493956 | 16000 | 50 | 1300 | 4 | 0 | 0.122313331592828 | 0.3381369468171625 | 1.35254778726865 | 0.764464471541578 | 0.263262884269469 | 0.152875007173279 | 0.152875007173279 | 10 | 9.34968512048945 | 0.125774919527583 | 0.123486709968187 | 0.01 | 0 | 1 | 1 | 4.70445267175557 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.103324919275474 0.319894299880718 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98994 | -13.2084 | 57623874.4085221 | 6159925.98070428 | -39843374.3292117 | 65740965.5093215 | 65.741 | 16 | 67.2894
gen_5045_1 | 83725310.62298449 | 1000 | 50 | 1300 | 4 | 0 | 0.150901294900104 | 0.2931414341859625 | 1.17256573674385 | 0.601463688726537 | 0.282160180495121 | 0.187590657388442 | 0.187590657388442 | 10 | 9.225314274639819 | 0.15217215720797 | 0.0534204910303466 | 0.01 | 0 | 1 | 1 | 3.97084814723791 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.135350074209971 0.593002652212512 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.07274 | -24.2464 | 7435417.17353323 | -308987.41889149 | -15343719.6063 | 5340221.7664 | 5.3402 | 1 | 83.7253
gen_5229_1 | 65762442.77972729 | 11000 | 50 | 1300 | 4 | 0 | 0.125010490226559 | 0.2976124256313775 | 1.19044970252551 | 0.763497128221812 | 0.322644502173923 | 0.176101364248898 | 0.176101364248898 | 10 | 6.73293403918971 | 0.0909491299521178 | 0.097808016075287 | 0.01 | 0 | 1 | 1 | 2.19749375593499 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.13622060100215 0.381984546021139 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98622 | -17.0292 | 45994681.1998802 | 1321563.10736672 | -13739466.1876559 | 25962507.4446783 | 25.9625 | 11 | 65.7624
gen_5230_2 | 36144729.3923702 | 11000 | 50 | 1300 | 4 | 0 | 0.153669304103823 | 0.33397639319566 | 1.33590557278264 | 0.915428744871658 | 0.365363388416171 | 0.213989995891694 | 0.213989995891694 | 10 | 6.12523303502239 | 0.102987064241897 | 0.0965313172165304 | 0.01 | 0 | 1 | 1 | 3.28062221393734 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.139380181227671 0.424489421675215 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98727 | -22.5776 | 0 | 1593404.15728837 | -7257341.34119935 | 15655531.2086362 | 15.6555 | 11 | 36.1447
gen_5231_1 | 32946558.3476471 | 11000 | 50 | 1300 | 4 | 0 | 0.201959629971534 | 0.3720311078469975 | 1.48812443138799 | 0.74173240119312 | 0.345077492259443 | 0.312922025034204 | 0.312922025034204 | 10 | 5.61352256229613 | 0.0102467300137505 | 0.0100398460892029 | 0.01 | 0 | 1 | 1 | 4.01807729780488 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.115702980337292 0.245185146695003 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.98153 | -8.644 | 26478867.7188798 | -4810241.36099475 | -11541152.5720352 | 11953001.3476595 | 11.953 | 11 | 32.9466
gen_5233_3 | 34046855.5721222 | 11000 | 50 | 1300 | 4 | 0 | 0.20698387010023 | 0.3603165998380875 | 1.44126639935235 | 0.739921911919257 | 0.334961609239457 | 0.305760274389759 | 0.305760274389759 | 10 | 6.05379235495231 | 0.0102200157905463 | 0.0102656072343234 | 0.01 | 0 | 1 | 1 | 4.04112954632146 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.103846765680169 0.247347393259406 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.01403 | -8.3081 | 28290144.3598012 | 3038663.34651271 | -10834745.8300074 | 8065644.633768409 | 8.0656 | 11 | 34.0469
gen_5234_1 | 16386692.7560885 | 11000 | 50 | 1300 | 4 | 0 | 0.201951610031538 | 0.3727677593976425 | 1.49107103759057 | 0.921757557777688 | 0.303159159672447 | 0.268113687559031 | 0.268113687559031 | 10 | 5.64482695443556 | 0.050517378540244 | 0.0522233921196312 | 0.01 | 0 | 1 | 1 | 3.23149796708208 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0610244330719579 0.309846977207577 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00599 | -13.0718 | 13345418.7931493 | -167070.114086708 | -5459655.31480033 | 6282474.35201425 | 6.2825 | 11 | 16.3867
gen_5235_1 | 32555253.9895289 | 11000 | 50 | 1300 | 4 | 0 | 0.140295098836534 | 0.2869998430705175 | 1.14799937228207 | 0.769669891044311 | 0.298827058867458 | 0.197526443671156 | 0.197526443671156 | 10 | 5.58797247438924 | 0.0510988949274179 | 0.0827419097926468 | 0.01 | 0 | 1 | 1 | 2.6615870565176 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.09009034515637911 0.419124758634716 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 0.99813 | -10.0054 | 21907119.1165335 | -1672272.54103906 | -9615301.83150899 | 15337314.3838458 | 15.3373 | 11 | 32.5553
gen_5236_2 | 31920388.7789045 | 11000 | 50 | 1300 | 4 | 0 | 0.146810719989706 | 0.2764931506459825 | 1.10597260258393 | 0.763595954369288 | 0.296021782608586 | 0.197912716191891 | 0.197912716191891 | 10 | 5.56003692662343 | 0.0521085245034192 | 0.08112469797395171 | 0.01 | 0 | 1 | 1 | 2.6100362072587 | 0 | 0 | [0 0 0 0] | [0 0 0 0] | [0 0 0 0] | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 3 | 2 | [0.8 0.0920970805417746 0.402873759800568 0 0 0 0 0 0 0] | [0.8 1 1.2 0 0 0 0 0 0 0] | [0.595 1 0 0 0 0 0 0 0 0] | [0.8 1.27 0 0 0 0 0 0 0 0] | 1 | 1 | G | 1.00408 | -10.036 | 21921752.2649333 | -147830.591569655 | -9664504.731958728 | 15511989.2131266 | 15.512 | 11 | 31.9204